## Annualised Power Consumption
Timestamp | Total Incoming
2021-12-31 | 3434907.8564
2022-12-31 | 655170.6532

## Incomer Sources
0
Generator | 574242.4
Mains | 3515836.1096

## SEU Data
0
HVAC | 48.7619
IT Load | 15.1144
Small Power and Other | 36.1237

## TEM1 Target Parameters w
R2 = 0.8406042923062046
const | -36.3991
CT2_TEM1_B.GCL_B_Meter#Real Energy Into the Load#kWh | 3.5012
CT2_TEM1_C.GCL_C_Meter#Real Energy Into the Load#kWh | 4.3267
CT2_TEM1_D.GCL_D_Meter#Real Energy Into the Load#kWh | 8.5915

## TEM1 Fitting Parameters w
R2 = 0.9320653627478636
const | -40.7366
CT2_TEM1_B.GCL_B_Meter#Real Energy Into the Load#kWh | -5.9465
CT2_TEM1_C.GCL_C_Meter#Real Energy Into the Load#kWh | 5.4758
CT2_TEM1_D.GCL_D_Meter#Real Energy Into the Load#kWh | 23.6098

## TEM2 Target Parameters w
R2 = 0.8884787214908691
const | -26.2966
CT2_TEM1_A.GCL_A_Meter#Real Energy Into the Load#kWh | -11.9654
CT2_TEM2_A.GCL_A_Meter#Real Energy Into the Load#kWh | 15.3587
CT2_TEM2_D.GCL_D_Meter#Real Energy Into the Load#kWh | 7.2783

## TEM2 Fitting Parameters w
R2 = 0.9096806309564804
const | -80.5219
CT2_TEM1_A.GCL_A_Meter#Real Energy Into the Load#kWh | -5.9445
CT2_TEM2_A.GCL_A_Meter#Real Energy Into the Load#kWh | 19.6769
CT2_TEM2_D.GCL_D_Meter#Real Energy Into the Load#kWh | 8.9432

## Total Target Parameters w
R2 = 0.8888346575539752
const | -43.041
CT2_TEM1_A.GCL_A_Meter#Real Energy Into the Load#kWh | -20.309
CT2_TEM1_D.GCL_D_Meter#Real Energy Into the Load#kWh | 31.7848
CT2_TEM2_A.GCL_A_Meter#Real Energy Into the Load#kWh | 14.9582
CT2_TEM2_D.GCL_D_Meter#Real Energy Into the Load#kWh | 6.1117

## Total Fitting Parameters w
R2 = 0.8979974181785412
const | -111.3582
CT2_TEM1_A.GCL_A_Meter#Real Energy Into the Load#kWh | -12.0876
CT2_TEM1_D.GCL_D_Meter#Real Energy Into the Load#kWh | 31.9624
CT2_TEM2_A.GCL_A_Meter#Real Energy Into the Load#kWh | 18.775
CT2_TEM2_D.GCL_D_Meter#Real Energy Into the Load#kWh | 9.079

## Plotting Data
| Timestamp | TEM | Actual HVAC Power kWh | Predicted HVAC Power kWh | Target HVAC Power kWh | Difference kWh | Cusum kWh | ENPI | PUE | Target PUE | Total UPS Power | Total Incoming Power
0 | 2021-03-14 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
1 | 2021-03-21 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
2 | 2021-03-28 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
3 | 2021-04-04 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 | 0 | 4.2127e+19 | 0 | 0
4 | 2021-04-11 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | -1.3217e-18 | 0
5 | 2021-04-18 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
6 | 2021-04-25 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
7 | 2021-05-02 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
8 | 2021-05-09 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
9 | 2021-05-16 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
10 | 2021-05-23 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
11 | 2021-05-30 | TEM1 | 0 | -40.7366 |  | 40.7366 |  | 0 |  | -inf | 0 | 0
12 | 2021-06-06 | TEM1 | 0 | -40.7366 |  | 40.7366 | 40.7366 | 0 |  | -inf | 0 | 0
13 | 2021-06-13 | TEM1 | 0 | -40.7366 |  | 40.7366 | 81.4732 | 0 |  | -inf | 0 | 0
14 | 2021-06-20 | TEM1 | 0 | -40.7366 |  | 40.7366 | 122.2098 | 0 |  | -inf | 0 | 0
15 | 2021-06-27 | TEM1 | 0 | -40.7366 |  | 40.7366 | 162.9463 | 0 |  | -inf | 0 | 0
16 | 2021-07-04 | TEM1 | 0 | -40.7366 |  | 40.7366 | 203.6829 | 0 |  | -inf | 0 | 0
17 | 2021-07-11 | TEM1 | 0 | -40.7366 |  | 40.7366 | 244.4195 | 0 |  | -inf | 0 | 0
18 | 2021-07-18 | TEM1 | 0.024745 | -40.6903 |  | 40.7151 | 285.1346 | -0.00060814 | 1.5328 | -66.2394 | 0.0098384 | 0.023452
19 | 2021-07-25 | TEM1 | 0.00054875 | -40.7345 |  | 40.7351 | 325.8696 | -1.3471e-05 | 6.2056 | -24.3682 | 0.0024154 | 0.0042744
20 | 2021-08-01 | TEM1 | 0.00054875 | -40.7345 |  | 40.7351 | 366.6047 | -1.3471e-05 | 1.6431 | -2.2845 | 0.0024154 | 0.0042744
21 | 2021-08-08 | TEM1 | 0.00054875 | -40.7345 |  | 40.7351 | 407.3397 | -1.3471e-05 | 3.8623 | 9.3274 | 1.0027 | 4.6724
22 | 2021-08-15 | TEM1 | 0.098281 | -39.4297 |  | 39.528 | 446.8677 | -0.0024926 | 28.0655 | 13.8912 | 1.1326 | 14.7279
23 | 2021-08-22 | TEM1 | 2.8731 | 41.2398 | 2.8731 | -38.3667 | 408.501 | 0.069668 | 23.3551 | 20.2069 | 5.3049 | 21.5526
24 | 2021-08-29 | TEM1 | 22.1831 | -16.7953 |  | 38.9784 | 447.4794 | -1.3208 | 12.3506 | 12.4938 | 8.0897 | 58.1132
25 | 2021-09-05 | TEM1 | 22.5379 | -13.5604 |  | 36.0983 | 483.5777 | -1.662 | 11.4734 | 10.4662 | 12.6073 | 474.2687
26 | 2021-09-12 | TEM1 | 85.9511 | 90.9404 | 85.9511 | -4.9893 | 478.5884 | 0.94514 | 11.5995 | 10.891 | 26.3927 | 799.894
27 | 2021-09-19 | TEM1 | 226.599 | 311.8347 | 226.599 | -85.2357 | 393.3527 | 0.72666 | 6.3687 | 6.9481 | 78.6885 | 399.7416
28 | 2021-09-26 | TEM1 | 981.8235 | 937.2009 |  | 44.6226 | 437.9754 | 1.0476 | 8.2693 | 8.7623 | 130.3055 | 1419.4756
29 | 2021-10-03 | TEM1 | 874.5266 | 766.3467 |  | 108.1799 | 546.1552 | 1.1412 | 8.9046 | 7.5555 | 143.8209 | 1329.5909
30 | 2021-10-10 | TEM1 | 9.495 | 45.7028 | 9.495 | -36.2078 | 509.9474 | 0.20776 | 5.2333 | 7.5978 | 21.4186 | 117.8792
31 | 2021-10-17 | TEM1 | 26.247 | 120.1177 | 26.247 | -93.8707 | 416.0767 | 0.21851 | 5.2869 | 9.1959 | 26.817 | 146.8622
32 | 2021-10-24 | TEM1 | 43.6415 | 65.6497 | 43.6415 | -22.0082 | 394.0685 | 0.66476 | 4.9773 | 5.4374 | 34.7418 | 159.4027
33 | 2021-10-31 | TEM1 | 21.7513 | 55.7616 | 21.7513 | -34.0103 | 360.0582 | 0.39008 | 4.4111 | 6.9788 | 36.3291 | 163.5628
34 | 2021-11-07 | TEM1 | 11.4924 | 54.9715 | 11.4924 | -43.4791 | 316.5791 | 0.20906 | 4.4829 | 6.0327 | 36.511 | 149.3488
35 | 2021-11-14 | TEM1 | 553.7171 | 571.3274 | 553.7171 | -17.6103 | 298.9688 | 0.96918 | 6.0556 | 5.361 | 152.281 | 841.7407
36 | 2021-11-21 | TEM1 | 684.0297 | 640.0602 |  | 43.9695 | 342.9383 | 1.0687 | 7.4028 | 6.8875 | 149.1742 | 1027.6841
37 | 2021-11-28 | TEM1 | 30.5228 | 138.0505 | 30.5228 | -107.5277 | 235.4106 | 0.2211 | 4.5701 | 6.648 | 49.3311 | 155.6381
38 | 2021-12-05 | TEM1 | 20.3113 | 64.5349 | 20.3113 | -44.2235 | 191.1871 | 0.31473 | 5.311 | 8.0214 | 32.4111 | 123.6817
39 | 2021-12-12 | TEM1 | 132.0809 | 214.3651 | 132.0809 | -82.2842 | 108.9029 | 0.61615 | 5.1558 | 5.6251 | 63.8293 | 275.6957
40 | 2021-12-19 | TEM1 | 24.0451 | 77.7556 | 24.0451 | -53.7105 | 55.1924 | 0.30924 | 4.7065 | 6.6314 | 33.8939 | 132.6018
41 | 2021-12-26 | TEM1 | 25.5757 | 98.9325 | 25.5757 | -73.3567 | -18.1643 | 0.25852 | 4.9698 | 7.3828 | 33.3416 | 144.4785
42 | 2022-01-02 | TEM1 | 22.5198 | 183.7541 | 22.5198 | -161.2343 | -179.3987 | 0.12255 | 5.2612 | 7.4764 | 28.0233 | 120.6266
43 | 2022-01-09 | TEM1 | 28.7139 | 37.7213 | 28.7139 | -9.0073 | -188.406 | 0.76121 | 5.8292 | 5.5266 | 32.0014 | 136.0456
44 | 2022-01-16 | TEM1 | 23.4076 | 8.9283 |  | 14.4794 | -173.9267 | 2.6217 | 3.4861 | 4.012 | 34.5914 | 134.8488
45 | 2022-01-23 | TEM1 | 68.9525 | 23.1923 |  | 45.7602 | -128.1664 | 2.9731 | 4.6732 | 4.2139 | 52.6855 | 214.6794
46 | 2022-01-30 | TEM1 | 125.5149 | 60.6854 |  | 64.8296 | -63.3369 | 2.0683 | -4.752 | -4.79 | 47.3148 | 262.1364
47 | 2022-02-06 | TEM1 | 156.211 | 82.5803 |  | 73.6307 | 10.2939 | 1.8916 | 6.0638 | 5.0904 | 57.7768 | 318.3587
48 | 2022-02-13 | TEM1 | 65.4885 | 149.1595 | 65.4885 | -83.671 | -73.3771 | 0.43905 | 4.4468 | 4.7199 | 42.0086 | 211.0963
49 | 2022-02-20 | TEM1 | 63.0223 | 40.4877 |  | 22.5346 | -50.8425 | 1.5566 | 3.8969 | 3.0664 | 40.5628 | 206.5955
50 | 2022-02-27 | TEM1 | 58.377 | 13.7957 |  | 44.5813 | -6.2612 | 4.2315 | 4.0563 | 4.2447 | 39.8144 | 210.8767
51 | 2022-03-06 | TEM1 | 44.5786 | 39.8082 |  | 4.7704 | -1.4908 | 1.1198 | 4.9325 | 5.6185 | 36.6159 | 185.3448
52 | 2022-03-13 | TEM1 | 42.8156 | 41.3248 |  | 1.4908 | -3.4106e-12 | 1.0361 | 5.7664 | 5.0873 | 31.9735 | 184.1806
0 | 2021-03-14 | TEM2 | -0.00098694 | -80.5219 |  | 80.5209 |  | 1.2257e-05 |  | -inf | 0 | 0
1 | 2021-03-21 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
2 | 2021-03-28 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
3 | 2021-04-04 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 | 0 | 4.2127e+19 | -2.6434e-18 | 0
4 | 2021-04-11 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 2.6434e-18 | 0
5 | 2021-04-18 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
6 | 2021-04-25 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
7 | 2021-05-02 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
8 | 2021-05-09 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
9 | 2021-05-16 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
10 | 2021-05-23 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
11 | 2021-05-30 | TEM2 | 0 | -80.5219 |  | 80.5219 |  | 0 |  | -inf | 0 | 0
12 | 2021-06-06 | TEM2 | 0 | -80.5219 |  | 80.5219 | 80.5219 | 0 |  | -inf | 0 | 0
13 | 2021-06-13 | TEM2 | 0 | -80.5219 |  | 80.5219 | 161.0438 | 0 |  | -inf | 0 | 0
14 | 2021-06-20 | TEM2 | 0 | -80.5219 |  | 80.5219 | 241.5658 | 0 |  | -inf | 0 | 0
15 | 2021-06-27 | TEM2 | 0 | -80.5219 |  | 80.5219 | 322.0877 | 0 |  | -inf | 0 | 0
16 | 2021-07-04 | TEM2 | 0 | -80.5219 |  | 80.5219 | 402.6096 | 0 |  | -inf | 0 | 0
17 | 2021-07-11 | TEM2 | 0 | -80.5219 |  | 80.5219 | 483.1315 | 0 |  | -inf | 0 | 0
18 | 2021-07-18 | TEM2 | 0.52507 | -80.456 |  | 80.9811 | 564.1126 | -0.0065262 | 1.5328 | -66.2394 | 1.6396 | 2.5049
19 | 2021-07-25 | TEM2 | 2.8367 | -80.5236 |  | 83.3603 | 647.4729 | -0.035228 | 6.2056 | -24.3682 | 3.7328 | 23.1747
20 | 2021-08-01 | TEM2 | 5.3288 | -8.677 |  | 14.0058 | 661.4787 | -0.61413 | 1.6431 | -2.2845 | 12.2536 | 20.1341
21 | 2021-08-08 | TEM2 | 23.0022 | 277.7332 | 23.0022 | -254.731 | 406.7477 | 0.082821 | 3.8623 | 9.3274 | 37.6962 | 144.7934
22 | 2021-08-15 | TEM2 | 6.0862 | -53.1668 |  | 59.253 | 466.0006 | -0.11447 | 28.0655 | 13.8912 | 5.1539 | 161.7076
23 | 2021-08-22 | TEM2 | 293.5475 | 99.3818 |  | 194.1656 | 660.1663 | 2.9537 | 23.3551 | 20.2069 | 35.8272 | 939.0887
24 | 2021-08-29 | TEM2 | 766.6022 | 844.0152 | 766.6022 | -77.4131 | 582.7532 | 0.90828 | 12.3506 | 12.4938 | 115.1759 | 1464.29
25 | 2021-09-05 | TEM2 | 1518.088 | 1365.8379 |  | 152.2501 | 735.0034 | 1.1115 | 11.4734 | 10.4662 | 192.425 | 1878.158
26 | 2021-09-12 | TEM2 | 1849.2078 | 1600.107 |  | 249.1007 | 984.1041 | 1.1557 | 11.5995 | 10.891 | 296.2066 | 2942.0934
27 | 2021-09-19 | TEM2 | 900.7678 | 1011.7566 | 900.7678 | -110.9888 | 873.1153 | 0.8903 | 6.3687 | 6.9481 | 229.6232 | 1563.8126
28 | 2021-09-26 | TEM2 | 49.7521 | 110.5406 | 49.7521 | -60.7885 | 812.3268 | 0.45008 | 8.2693 | 8.7623 | 67.6995 | 217.8872
29 | 2021-10-03 | TEM2 | 50.6333 | -83.0174 |  | 133.6507 | 945.9775 | -0.60991 | 8.9046 | 7.5555 | 24.6049 | 170.1809
30 | 2021-10-10 | TEM2 | 10.1499 | 93.1402 | 10.1499 | -82.9903 | 862.9872 | 0.10897 | 5.2333 | 7.5978 | 26.9328 | 135.1576
31 | 2021-10-17 | TEM2 | 7.7413 | 78.3038 | 7.7413 | -70.5625 | 792.4246 | 0.098862 | 5.2869 | 9.1959 | 26.7488 | 136.334
32 | 2021-10-24 | TEM2 | 11.4195 | 31.1996 | 11.4195 | -19.78 | 772.6446 | 0.36602 | 4.9773 | 5.4374 | 23.7446 | 131.7004
33 | 2021-10-31 | TEM2 | 21.3114 | 170.2212 | 21.3114 | -148.9099 | 623.7347 | 0.1252 | 4.4111 | 6.9788 | 41.1097 | 178.0265
34 | 2021-11-07 | TEM2 | 10.8794 | 37.7575 | 10.8794 | -26.8781 | 596.8567 | 0.28814 | 4.4829 | 6.0327 | 28.3182 | 141.2749
35 | 2021-11-14 | TEM2 | 42.112 | -128.0568 |  | 170.1688 | 767.0254 | -0.32885 | 6.0556 | 5.361 | 20.3132 | 203.4263
36 | 2021-11-21 | TEM2 | 42.5919 | -43.4483 |  | 86.0401 | 853.0656 | -0.98029 | 7.4028 | 6.8875 | 27.889 | 283.0773
37 | 2021-11-28 | TEM2 | 27.2538 | 187.9446 | 27.2538 | -160.6908 | 692.3748 | 0.14501 | 4.5701 | 6.648 | 53.3119 | 313.4555
38 | 2021-12-05 | TEM2 | 52.3893 | 243.662 | 52.3893 | -191.2726 | 501.1021 | 0.21501 | 5.311 | 8.0214 | 44.0805 | 282.5641
39 | 2021-12-12 | TEM2 | 101.4261 | 98.6166 |  | 2.8095 | 503.9116 | 1.0285 | 5.1558 | 5.6251 | 44.2586 | 281.5796
40 | 2021-12-19 | TEM2 | 105.7411 | 211.2636 | 105.7411 | -105.5225 | 398.3892 | 0.50052 | 4.7065 | 6.6314 | 55.761 | 289.3619
41 | 2021-12-26 | TEM2 | 132.6054 | 262.7779 | 132.6054 | -130.1726 | 268.2166 | 0.50463 | 4.9698 | 7.3828 | 59.849 | 318.6594
42 | 2022-01-02 | TEM2 | 94.0266 | 75.1157 |  | 18.9109 | 287.1275 | 1.2518 | 5.2612 | 7.4764 | 40.9337 | 242.1726
43 | 2022-01-09 | TEM2 | 111.6956 | 94.5653 |  | 17.1303 | 304.2578 | 1.1811 | 5.8292 | 5.5266 | 36.9991 | 266.1702
44 | 2022-01-16 | TEM2 | 149.5268 | 261.083 | 149.5268 | -111.5561 | 192.7016 | 0.57272 | 3.4861 | 4.012 | 113.3063 | 380.7435
45 | 2022-01-23 | TEM2 | 97.7385 | 100.6182 | 97.7385 | -2.8797 | 189.822 | 0.97138 | 4.6732 | 4.2139 | 56.6612 | 296.3172
46 | 2022-01-30 | TEM2 | 106.1773 | 210.9974 | 106.1773 | -104.8201 | 85.0019 | 0.50322 | -4.752 | -4.79 | 59.2875 | -768.7151
47 | 2022-02-06 | TEM2 | 140.6137 | 129.8108 |  | 10.8029 | 95.8048 | 1.0832 | 6.0638 | 5.0904 | 46.736 | 315.3823
48 | 2022-02-13 | TEM2 | 148.9973 | 86.2219 |  | 62.7754 | 158.5802 | 1.7281 | 4.4468 | 4.7199 | 80.2873 | 332.734
49 | 2022-02-20 | TEM2 | 167.558 | 94.685 |  | 72.873 | 231.4532 | 1.7696 | 3.8969 | 3.0664 | 102.9197 | 352.5423
50 | 2022-02-27 | TEM2 | 169.5593 | 291.2505 | 169.5593 | -121.6912 | 109.762 | 0.58218 | 4.0563 | 4.2447 | 102.6907 | 367.1678
51 | 2022-03-06 | TEM2 | 185.7387 | 306.4126 | 185.7387 | -120.6739 | -10.9118 | 0.60617 | 4.9325 | 5.6185 | 72.0444 | 350.6261
52 | 2022-03-13 | TEM2 | 171.4114 | 160.4995 |  | 10.9118 | 5.8549e-12 | 1.068 | 5.7664 | 5.0873 | 55 | 317.3472
0 | 2021-03-14 | Total | -0.00098694 | -111.3582 |  | 111.3572 |  | 8.8628e-06 |  | -inf | 0 | 0
1 | 2021-03-21 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
2 | 2021-03-28 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
3 | 2021-04-04 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 | 0 | 4.2127e+19 | -2.6434e-18 | 1.3217e-18
4 | 2021-04-11 | Total | -8.4588e-17 | -111.3582 |  | 111.3582 |  | 7.5961e-19 |  | -inf | -2.6434e-18 | 0
5 | 2021-04-18 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
6 | 2021-04-25 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
7 | 2021-05-02 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
8 | 2021-05-09 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
9 | 2021-05-16 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
10 | 2021-05-23 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
11 | 2021-05-30 | Total | 0 | -111.3582 |  | 111.3582 |  | 0 |  | -inf | 0 | 0
12 | 2021-06-06 | Total | 0 | -111.3582 |  | 111.3582 | 111.3582 | 0 |  | -inf | 0 | 0
13 | 2021-06-13 | Total | 0 | -111.3582 |  | 111.3582 | 222.7163 | 0 |  | -inf | 0 | 0
14 | 2021-06-20 | Total | 0 | -111.3582 |  | 111.3582 | 334.0745 | 0 |  | -inf | 0 | 0
15 | 2021-06-27 | Total | 0 | -111.3582 |  | 111.3582 | 445.4326 | 0 |  | -inf | 0 | 0
16 | 2021-07-04 | Total | 0 | -111.3582 |  | 111.3582 | 556.7908 | 0 |  | -inf | 0 | 0
17 | 2021-07-11 | Total | 0 | -111.3582 |  | 111.3582 | 668.1489 | 0 |  | -inf | 0 | 0
18 | 2021-07-18 | Total | 0.54981 | -111.2387 |  | 111.7885 | 779.9374 | -0.0049427 | 1.5328 | -66.2394 | 1.6495 | 2.5284
19 | 2021-07-25 | Total | 2.8372 | -111.3612 |  | 114.1985 | 894.1359 | -0.025478 | 6.2056 | -24.3682 | 3.7352 | 23.1789
20 | 2021-08-01 | Total | 5.3294 | -42.8078 |  | 48.1372 | 942.273 | -0.1245 | 1.6431 | -2.2845 | 12.2561 | 20.1384
21 | 2021-08-08 | Total | 23.0027 | 234.4968 | 23.0027 | -211.494 | 730.779 | 0.098094 | 3.8623 | 9.3274 | 38.699 | 149.4658
22 | 2021-08-15 | Total | 6.1845 | -82.923 |  | 89.1075 | 819.8865 | -0.074581 | 28.0655 | 13.8912 | 6.2866 | 176.4355
23 | 2021-08-22 | Total | 296.4206 | 166.9316 |  | 129.489 | 949.3755 | 1.7757 | 23.3551 | 20.2069 | 41.132 | 960.6413
24 | 2021-08-29 | Total | 788.7853 | 806.4417 | 788.7853 | -17.6564 | 931.7191 | 0.97811 | 12.3506 | 12.4938 | 123.2657 | 1522.4032
25 | 2021-09-05 | Total | 1540.6259 | 1334.117 |  | 206.5089 | 1138.228 | 1.1548 | 11.4734 | 10.4662 | 205.0323 | 2352.4267
26 | 2021-09-12 | Total | 1935.1589 | 1706.6151 |  | 228.5438 | 1366.7717 | 1.1339 | 11.5995 | 10.891 | 322.5992 | 3741.9875
27 | 2021-09-19 | Total | 1127.3668 | 1305.9876 | 1127.3668 | -178.6207 | 1188.151 | 0.86323 | 6.3687 | 6.9481 | 308.3117 | 1963.5542
28 | 2021-09-26 | Total | 1031.5757 | 1129.1848 | 1031.5757 | -97.6091 | 1090.5418 | 0.91356 | 8.2693 | 8.7623 | 198.005 | 1637.3628
29 | 2021-10-03 | Total | 925.1598 | 697.9308 |  | 227.2291 | 1317.7709 | 1.3256 | 8.9046 | 7.5555 | 168.4258 | 1499.7718
30 | 2021-10-10 | Total | 19.645 | 133.9745 | 19.645 | -114.3295 | 1203.4414 | 0.14663 | 5.2333 | 7.5978 | 48.3515 | 253.0368
31 | 2021-10-17 | Total | 33.9883 | 243.3761 | 33.9883 | -209.3878 | 994.0536 | 0.13965 | 5.2869 | 9.1959 | 53.5659 | 283.1962
32 | 2021-10-24 | Total | 55.061 | 81.9697 | 55.061 | -26.9087 | 967.1449 | 0.67172 | 4.9773 | 5.4374 | 58.4864 | 291.1031
33 | 2021-10-31 | Total | 43.0627 | 241.9041 | 43.0627 | -198.8414 | 768.3035 | 0.17802 | 4.4111 | 6.9788 | 77.4388 | 341.5893
34 | 2021-11-07 | Total | 22.3718 | 122.8405 | 22.3718 | -100.4687 | 667.8348 | 0.18212 | 4.4829 | 6.0327 | 64.8292 | 290.6237
35 | 2021-11-14 | Total | 595.8291 | 475.9319 |  | 119.8971 | 787.7319 | 1.2519 | 6.0556 | 5.361 | 172.5941 | 1045.167
36 | 2021-11-21 | Total | 726.6216 | 635.3887 |  | 91.2329 | 878.9648 | 1.1436 | 7.4028 | 6.8875 | 177.0632 | 1310.7614
37 | 2021-11-28 | Total | 57.7766 | 271.0572 | 57.7766 | -213.2806 | 665.6842 | 0.21315 | 4.5701 | 6.648 | 102.643 | 469.0937
38 | 2021-12-05 | Total | 72.7007 | 280.0262 | 72.7007 | -207.3255 | 458.3587 | 0.25962 | 5.311 | 8.0214 | 76.4916 | 406.2458
39 | 2021-12-12 | Total | 233.5071 | 284.2391 | 233.5071 | -50.7321 | 407.6266 | 0.82152 | 5.1558 | 5.6251 | 108.088 | 557.2753
40 | 2021-12-19 | Total | 129.7862 | 302.3641 | 129.7862 | -172.5779 | 235.0487 | 0.42924 | 4.7065 | 6.6314 | 89.6549 | 421.9637
41 | 2021-12-26 | Total | 158.1811 | 383.0465 | 158.1811 | -224.8654 | 10.1833 | 0.41296 | 4.9698 | 7.3828 | 93.1906 | 463.1379
42 | 2022-01-02 | Total | 116.5464 | 269.3002 | 116.5464 | -152.7538 | -142.5705 | 0.43278 | 5.2612 | 7.4764 | 68.9571 | 362.7992
43 | 2022-01-09 | Total | 140.4095 | 119.5318 |  | 20.8777 | -121.6929 | 1.1747 | 5.8292 | 5.5266 | 69.0006 | 402.2158
44 | 2022-01-16 | Total | 172.9345 | 250.7029 | 172.9345 | -77.7684 | -199.4613 | 0.6898 | 3.4861 | 4.012 | 147.8976 | 515.5923
45 | 2022-01-23 | Total | 166.6911 | 116.4681 |  | 50.223 | -149.2382 | 1.4312 | 4.6732 | 4.2139 | 109.3467 | 510.9965
46 | 2022-01-30 | Total | 231.6922 | 227.646 |  | 4.0462 | -145.192 | 1.0178 | -4.752 | -4.79 | 106.6023 | -506.5786
47 | 2022-02-06 | Total | 296.8248 | 195.0981 |  | 101.7267 | -43.4654 | 1.5214 | 6.0638 | 5.0904 | 104.5129 | 633.741
48 | 2022-02-13 | Total | 214.4858 | 247.8798 | 214.4858 | -33.394 | -76.8594 | 0.86528 | 4.4468 | 4.7199 | 122.2959 | 543.8303
49 | 2022-02-20 | Total | 230.5804 | 111.4136 |  | 119.1667 | 42.3074 | 2.0696 | 3.8969 | 3.0664 | 143.4825 | 559.1378
50 | 2022-02-27 | Total | 227.9363 | 254.7801 | 227.9363 | -26.8438 | 15.4636 | 0.89464 | 4.0563 | 4.2447 | 142.505 | 578.0445
51 | 2022-03-06 | Total | 230.3174 | 304.8511 | 230.3174 | -74.5338 | -59.0702 | 0.75551 | 4.9325 | 5.6185 | 108.6603 | 535.9709
52 | 2022-03-13 | Total | 214.227 | 155.1568 |  | 59.0702 | -2.4869e-12 | 1.3807 | 5.7664 | 5.0873 | 86.9735 | 501.5278