## Annualised Power Consumption
Timestamp | Total Incoming
2021-12-31 | 27746291.288
2022-12-31 | 5873658.6797

## Incomer Sources
0
Mains | 22057568.791
Generator | 224867.7578
Solar | 628432.8125

## SEU Data
0
HVAC | 16.4135
IT Load | 74.6207
Small Power and Other | 8.9658

## TEM1 Target Parameters w
R2 = 0.938007000172543
const | -0.25969
JB2_TEM1.J2_TEM_1_GCL_UPS_System_B#Real Energy Into the Load#kWh | -1.2657
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -4.3568
JB2_TEM4.JB2_TEM4_GCL_UPS_System_A#Real Energy Into the Load#kWh | -5.1638
JB2_TEM4.JB2_TEM4_UPS_System_A#Real Energy Into the Load#kWh | 624.9317

## TEM1 Fitting Parameters w
R2 = 0.8757197309014283
const | -2324.4434
JB2_TEM1.J2_TEM_1_GCL_UPS_System_B#Real Energy Into the Load#kWh | 1.2105
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -0.86257
JB2_TEM4.JB2_TEM4_GCL_UPS_System_A#Real Energy Into the Load#kWh | 1.9814
JB2_TEM4.JB2_TEM4_UPS_System_A#Real Energy Into the Load#kWh | 3287.2213

## TEM2 Target Parameters w
R2 = 0.8967679684537229
const | -1.9621
JB2_TEM2.JB2_TEM2_GCL_UPS_System_A#Real Energy Into the Load#kWh | 9.9672
JB2_TEM2.JB2_TEM2_GCL_UPS_System_B#Real Energy Into the Load#kWh | 20.1305
JB2_TEM2.JB2_TEM2_GCL_UPS_System_C#Real Energy Into the Load#kWh | 11.3113
JB2_TEM2.JB2_TEM2_UPS_System_C#Real Energy Into the Load#kWh | -2.4431

## TEM2 Fitting Parameters w
R2 = 0.955854769386295
const | -335.2359
JB2_TEM2.JB2_TEM2_GCL_UPS_System_A#Real Energy Into the Load#kWh | 13.9689
JB2_TEM2.JB2_TEM2_GCL_UPS_System_B#Real Energy Into the Load#kWh | 26.7465
JB2_TEM2.JB2_TEM2_GCL_UPS_System_C#Real Energy Into the Load#kWh | 21.4484
JB2_TEM2.JB2_TEM2_UPS_System_C#Real Energy Into the Load#kWh | -2.7741

## TEM3 Target Parameters w
R2 = 0.9910720632056407
const | -0.076647
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -0.38664
JB2_TEM3.J2_TEM3_UPS_System_A_Rectifier_Section#Real Energy Into the Load#kWh | -3.6026
JB2_TEM3.J2_TEM3_UPS_System_B#Real Energy Into the Load#kWh | 0.8376
JB2_TEM4.JB2_TEM4_GCL_UPS_System_C#Real Energy Into the Load#kWh | 0.40088

## TEM3 Fitting Parameters w
R2 = 0.9170669252884645
const | 382.8666
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -0.40238
JB2_TEM3.J2_TEM3_UPS_System_A_Rectifier_Section#Real Energy Into the Load#kWh | -7.0505
JB2_TEM3.J2_TEM3_UPS_System_B#Real Energy Into the Load#kWh | -1.1832
JB2_TEM4.JB2_TEM4_GCL_UPS_System_C#Real Energy Into the Load#kWh | 0.6992

## TEM4 Target Parameters w
R2 = 0.5807403042885211
const | -11.989
JB2_TEM2.JB2_TEM2_GCL_UPS_System_C#Real Energy Into the Load#kWh | 0.85483
JB2_TEM4.JB2_TEM4_GCL_UPS_System_A#Real Energy Into the Load#kWh | 5.7595
JB2_TEM4.JB2_TEM4_GCL_UPS_System_B#Real Energy Into the Load#kWh | 4.0125
JB2_TEM5.JB2_TEM5_GCL_UPS_System_E#Real Energy Into the Load#kWh | -2.1237

## TEM4 Fitting Parameters w
R2 = 0.8853650822230273
const | 116.9521
JB2_TEM2.JB2_TEM2_GCL_UPS_System_C#Real Energy Into the Load#kWh | -11.3944
JB2_TEM4.JB2_TEM4_GCL_UPS_System_A#Real Energy Into the Load#kWh | 8.5744
JB2_TEM4.JB2_TEM4_GCL_UPS_System_B#Real Energy Into the Load#kWh | 9.9481
JB2_TEM5.JB2_TEM5_GCL_UPS_System_E#Real Energy Into the Load#kWh | 18.4052

## TEM5 Target Parameters w
R2 = 0.4311403379100289
const | -0.13448
JB2_TEM2.JB2_TEM2_GCL_UPS_System_B#Real Energy Into the Load#kWh | -1.8576
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -1.8759
JB2_TEM3.J2_TEM3_UPS_System_C#Real Energy Into the Load#kWh | 0.62417
JB2_TEM4.JB2_TEM4_GCL_UPS_System_C#Real Energy Into the Load#kWh | 1.5572

## TEM5 Fitting Parameters w
R2 = 0.9478370182130327
const | 5488.3088
JB2_TEM2.JB2_TEM2_GCL_UPS_System_B#Real Energy Into the Load#kWh | -7.6907
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -6.9792
JB2_TEM3.J2_TEM3_UPS_System_C#Real Energy Into the Load#kWh | -27.0234
JB2_TEM4.JB2_TEM4_GCL_UPS_System_C#Real Energy Into the Load#kWh | 9.2482

## Total Target Parameters w
R2 = 0.8411447108140099
const | 7.8721
JB2_TEM1.J2_TEM_1_GCL_UPS_System_A#Real Energy Into the Load#kWh | 22.8476
JB2_TEM2.JB2_TEM2_SDB_UPS#Real Energy Into the Load#kWh | -1044.3849
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | 1.8167
JB2_TEM3.J2_TEM3_UPS_System_C_Rectifier_Section#Real Energy Into the Load#kWh | 117.0806

## Total Fitting Parameters w
R2 = 0.9857480775604982
const | 898.4534
JB2_TEM1.J2_TEM_1_GCL_UPS_System_A#Real Energy Into the Load#kWh | 8.8863
JB2_TEM2.JB2_TEM2_SDB_UPS#Real Energy Into the Load#kWh | -1434.1868
JB2_TEM3.J2_TEM3_Mechanical_UPS_System_A#Real Energy Into the Load#kWh | -17.5297
JB2_TEM3.J2_TEM3_UPS_System_C_Rectifier_Section#Real Energy Into the Load#kWh | 360.1028

## Plotting Data
| Timestamp | TEM | Actual HVAC Power kWh | Predicted HVAC Power kWh | Target HVAC Power kWh | Difference kWh | Cusum kWh | ENPI | PUE | Target PUE | Total UPS Power | Total Incoming Power
0 | 2021-01-03 | TEM1 | 285.692 | -62.9958 |  | 348.6878 |  | -4.5351 | 1.4108 | 1.8546 | 1101.839 | 1336.2817
1 | 2021-01-10 | TEM1 | 293.1694 | -42.3295 |  | 335.4989 |  | -6.9259 | 1.4195 | 1.8655 | 1125.9674 | 1375.6012
2 | 2021-01-17 | TEM1 | 282.5039 | -39.4484 |  | 321.9522 |  | -7.1614 | 1.4132 | 1.9613 | 1121.1942 | 1358.2976
3 | 2021-01-24 | TEM1 | 296.7053 | -32.3593 |  | 329.0646 |  | -9.1691 | 1.4138 | 1.8973 | 1121.6813 | 1347.6284
4 | 2021-01-31 | TEM1 | 280.6372 | -39.9415 |  | 320.5788 |  | -7.0262 | 1.4304 | 1.8774 | 1123.7884 | 1419.1607
5 | 2021-02-07 | TEM1 | 269.895 | 132.1944 |  | 137.7006 |  | 2.0417 | 1.4226 | 1.8857 | 1124.5988 | 1412.6607
6 | 2021-02-14 | TEM1 | 285.6232 | 228.3351 |  | 57.2881 |  | 1.2509 | 1.403 | 1.8264 | 1123.2197 | 1359.5508
7 | 2021-02-21 | TEM1 | 296.9343 | 247.1369 |  | 49.7974 |  | 1.2015 | 1.3965 | 1.8307 | 1125.2903 | 1346.4048
8 | 2021-02-28 | TEM1 | 272.7733 | 254.2769 |  | 18.4964 |  | 1.0727 | 1.3977 | 1.7912 | 1136.7824 | 1398.4447
9 | 2021-03-07 | TEM1 | 282.5632 | 253.0555 |  | 29.5078 |  | 1.1166 | 1.3783 | 1.7335 | 1143.314 | 1367.3492
10 | 2021-03-14 | TEM1 | 304.8805 | 264.6641 |  | 40.2164 |  | 1.152 | 1.3989 | 1.7639 | 1138.8326 | 1370.3424
11 | 2021-03-21 | TEM1 | 278.4096 | 255.0647 |  | 23.3449 |  | 1.0915 | 1.3944 | 1.8022 | 1137.8336 | 1385.744
12 | 2021-03-28 | TEM1 | 269.7355 | 244.7964 |  | 24.9391 |  | 1.1019 | 1.3818 | 1.7839 | 1140.3364 | 1400.8393
13 | 2021-04-04 | TEM1 | 280.9508 | 263.8875 |  | 17.0633 |  | 1.0647 | 1.3785 | 1.7869 | 1144.883 | 1382.5298
14 | 2021-04-11 | TEM1 | 287.2841 | 243.982 |  | 43.3021 |  | 1.1775 | 1.3807 | 1.7222 | 1146.1659 | 1391.7381
15 | 2021-04-18 | TEM1 | 271.8732 | 247.3369 |  | 24.5363 |  | 1.0992 | 1.3844 | 1.627 | 1146.3493 | 1385.4482
16 | 2021-04-25 | TEM1 | 256.5897 | 260.7044 | 256.5897 | -4.1146 |  | 0.98422 | 1.348 | 1.4462 | 1152.7365 | 1380.881
17 | 2021-05-02 | TEM1 | 257.7572 | 237.2222 |  | 20.535 |  | 1.0866 | 1.3315 | 1.4379 | 1155.4347 | 1390.3929
18 | 2021-05-09 | TEM1 | 236.0193 | 232.9986 |  | 3.0207 |  | 1.013 | 1.3132 | 1.4542 | 1160.0043 | 1369.25
19 | 2021-05-16 | TEM1 | 269.3079 | 251.449 |  | 17.8589 |  | 1.071 | 1.34 | 1.4823 | 1162.8475 | 1406.4591
20 | 2021-05-23 | TEM1 | 241.7332 | 236.3014 |  | 5.4317 |  | 1.023 | 1.2917 | 1.3952 | 1176.7378 | 1393.2914
21 | 2021-05-30 | TEM1 | 249.5978 | 236.8656 |  | 12.7321 |  | 1.0538 | 1.2837 | 1.3276 | 1177.1196 | 1406.9048
22 | 2021-06-06 | TEM1 | 141.0401 | 234.5074 | 141.0401 | -93.4674 |  | 0.60143 | 1.2458 | 1.4569 | 1175.2194 | 1324.452
23 | 2021-06-13 | TEM1 | 203.8857 | 242.0133 | 203.8857 | -38.1276 |  | 0.84246 | 1.2973 | 1.4167 | 1173.7533 | 1417.8741
24 | 2021-06-20 | TEM1 | 236.6183 | 245.0718 | 236.6183 | -8.4535 |  | 0.96551 | 1.3322 | 1.4209 | 1171.4299 | 1415.5134
25 | 2021-06-27 | TEM1 | 215.7192 | 231.2458 | 215.7192 | -15.5265 |  | 0.93286 | 1.3067 | 1.3834 | 1174.8671 | 1381.1548
26 | 2021-07-04 | TEM1 | 275.2099 | 245.1968 |  | 30.0131 |  | 1.1224 | 1.3516 | 1.458 | 1176.3354 | 1441.619
27 | 2021-07-11 | TEM1 | 261.4301 | 235.5917 |  | 25.8384 |  | 1.1097 | 1.3281 | 1.3655 | 1175.5073 | 1440.8333
28 | 2021-07-18 | TEM1 | 205.9417 | 243.8978 | 205.9417 | -37.9561 |  | 0.84438 | 1.2788 | 1.3906 | 1171.1765 | 1380.1096
29 | 2021-07-25 | TEM1 | 141.5483 | 235.6987 | 141.5483 | -94.1504 |  | 0.60055 | 1.2438 | 1.3943 | 1172.5258 | 1302.75
30 | 2021-08-01 | TEM1 | 239.3732 | 237.6093 |  | 1.7639 |  | 1.0074 | 1.2993 | 1.4316 | 1174.6446 | 1405.9643
31 | 2021-08-08 | TEM1 | 304.5037 | 236.9147 |  | 67.589 |  | 1.2853 | 1.3491 | 1.4418 | 1173.2733 | 1474.7857
32 | 2021-08-15 | TEM1 | 214.6624 | 238.633 | 214.6624 | -23.9707 |  | 0.89955 | 1.3084 | 1.4593 | 1169.2796 | 1407.1429
33 | 2021-08-22 | TEM1 | 302.2352 | 237.1442 |  | 65.091 |  | 1.2745 | 1.3484 | 1.4263 | 1165.8154 | 1445.0357
34 | 2021-08-29 | TEM1 | 332.4444 | 247.2571 |  | 85.1873 |  | 1.3445 | 1.365 | 1.4744 | 1162.1248 | 1480.1263
35 | 2021-09-05 | TEM1 | 284.5463 | 229.1096 |  | 55.4367 |  | 1.242 | 1.3471 | 1.423 | 1168.489 | 1420.7857
36 | 2021-09-12 | TEM1 | 343.9286 | 245.1727 |  | 98.7559 |  | 1.4028 | 1.3729 | 1.4675 | 1168.9769 | 1498.7143
37 | 2021-09-19 | TEM1 | 324.7557 | 242.5324 |  | 82.2232 |  | 1.339 | 1.3584 | 1.424 | 1173.3171 | 1467.0964
38 | 2021-09-26 | TEM1 | 361.3484 | 248.8748 |  | 112.4737 |  | 1.4519 | 1.3777 | 1.4354 | 1175.0107 | 1498.9286
39 | 2021-10-03 | TEM1 | 375.5511 | 250.5844 |  | 124.9667 |  | 1.4987 | 1.3818 | 1.4192 | 1180.3645 | 1537.8571
40 | 2021-10-10 | TEM1 | 354.7232 | 232.7451 |  | 121.9781 |  | 1.5241 | 1.3576 | 1.424 | 1182.8597 | 1487.3987
41 | 2021-10-17 | TEM1 | 357.065 | 244.7327 |  | 112.3323 |  | 1.459 | 1.3643 | 1.4421 | 1180.7631 | 1461.1017
42 | 2021-10-24 | TEM1 | 288.628 | 229.2852 |  | 59.3428 |  | 1.2588 | 1.3288 | 1.4661 | 1182.883 | 1404.1539
43 | 2021-10-31 | TEM1 | 277.9032 | 234.9792 |  | 42.924 |  | 1.1827 | 1.3453 | 1.4276 | 1181.0887 | 1448.3926
44 | 2021-11-07 | TEM1 | 308.9644 | 250.9266 |  | 58.0379 |  | 1.2313 | 1.3571 | 1.4237 | 1180.5177 | 1411.7499
45 | 2021-11-14 | TEM1 | 298.9655 | 247.097 |  | 51.8685 |  | 1.2099 | 1.3621 | 1.4241 | 1181.5389 | 1437.9905
46 | 2021-11-21 | TEM1 | 309.0701 | 242.5985 |  | 66.4715 |  | 1.274 | 1.3799 | 1.376 | 1186.5928 | 1470.873
47 | 2021-11-28 | TEM1 | 275.6037 | 235.0254 |  | 40.5783 |  | 1.1727 | 1.3435 | 1.356 | 1192.2317 | 1451.0714
48 | 2021-12-05 | TEM1 | 297.9882 | 247.5128 |  | 50.4754 |  | 1.2039 | 1.3538 | 1.3403 | 1183.5038 | 1430.3553
49 | 2021-12-12 | TEM1 | 296.5791 | 251.8247 |  | 44.7544 |  | 1.1777 | 1.3556 | 1.3601 | 1187.1935 | 1435.6429
50 | 2021-12-19 | TEM1 | 281.9596 | 279.6446 |  | 2.315 |  | 1.0083 | 1.341 | 1.3456 | 1189.0827 | 1455.5357
51 | 2021-12-26 | TEM1 | 292.2582 | 309.3404 | 292.2582 | -17.0822 |  | 0.94478 | 1.3329 | 1.2952 | 1190.2864 | 1429.881
52 | 2022-01-02 | TEM1 | 303.7684 | 298.848 |  | 4.9204 | 4.9204 | 1.0165 | 1.3469 | 1.3265 | 1189.413 | 1426.3571
53 | 2022-01-09 | TEM1 | 292.8246 | 294.7844 | 292.8246 | -1.9598 | 2.9607 | 0.99335 | 1.3417 | 1.3414 | 1195.1724 | 1440.3095
54 | 2022-01-16 | TEM1 | 298.5486 | 298.7864 | 298.5486 | -0.23778 | 2.7229 | 0.9992 | 1.3549 | 1.3562 | 1199.7074 | 1455.5714
55 | 2022-01-23 | TEM1 | 289.8139 | 290.7825 | 289.8139 | -0.96857 | 1.7543 | 0.99667 | 1.333 | 1.3359 | 1202.7909 | 1442.0703
56 | 2022-01-30 | TEM1 | 294.4299 | 294.3513 |  | 0.078538 | 1.8329 | 1.0003 | 1.3444 | 1.3428 | 1202.6734 | 1460.0238
57 | 2022-02-06 | TEM1 | 306.1975 | 302.6985 |  | 3.499 | 5.3319 | 1.0116 | 1.356 | 1.3536 | 1201.0893 | 1482.4106
58 | 2022-02-13 | TEM1 | 302.9841 | 306.9982 | 302.9841 | -4.014 | 1.3178 | 0.98692 | 1.3407 | 1.3437 | 1199.7611 | 1439.8333
59 | 2022-02-20 | TEM1 | 297.192 | 297.3926 | 297.192 | -0.20058 | 1.1172 | 0.99933 | 1.3451 | 1.3425 | 1199.3098 | 1451.9775
60 | 2022-02-27 | TEM1 | 305.8008 | 307.1066 | 305.8008 | -1.3058 | -0.18856 | 0.99575 | 1.3466 | 1.3496 | 1202.754 | 1466.9524
61 | 2022-03-06 | TEM1 | 300.6648 | 295.5789 |  | 5.0859 | 4.8974 | 1.0172 | 1.3386 | 1.3368 | 1208.9689 | 1466.1905
62 | 2022-03-13 | TEM1 | 273.1744 | 274.4694 | 273.1744 | -1.295 | 3.6024 | 0.99528 | 1.3259 | 1.3246 | 1209.2275 | 1501
0 | 2021-01-03 | TEM2 | 22.6109 | -288.9992 |  | 311.6101 |  | -0.078239 | 1.4108 | 1.8546 | 67.851 | 143.5185
1 | 2021-01-10 | TEM2 | 44.7794 | -199.762 |  | 244.5414 |  | -0.22416 | 1.4195 | 1.8655 | 73.2259 | 170.0342
2 | 2021-01-17 | TEM2 | 58.5503 | -31.6578 |  | 90.2082 |  | -1.8495 | 1.4132 | 1.9613 | 80.9611 | 193.115
3 | 2021-01-24 | TEM2 | 42.5044 | -29.4284 |  | 71.9328 |  | -1.4443 | 1.4138 | 1.8973 | 82.0388 | 176.9833
4 | 2021-01-31 | TEM2 | 34.9852 | -121.3033 |  | 156.2885 |  | -0.28841 | 1.4304 | 1.8774 | 82.2077 | 171.234
5 | 2021-02-07 | TEM2 | 19.9941 | -130.8409 |  | 150.835 |  | -0.15281 | 1.4226 | 1.8857 | 120.6936 | 196.0848
6 | 2021-02-14 | TEM2 | 60.91 | -41.838 |  | 102.748 |  | -1.4559 | 1.403 | 1.8264 | 145.2288 | 259.9565
7 | 2021-02-21 | TEM2 | 71.5489 | 25.9838 |  | 45.5651 |  | 2.7536 | 1.3965 | 1.8307 | 199.8028 | 325.721
8 | 2021-02-28 | TEM2 | 69.8673 | 10.5629 |  | 59.3045 |  | 6.6144 | 1.3977 | 1.7912 | 228.2381 | 354.828
9 | 2021-03-07 | TEM2 | 31.5525 | -63.074 |  | 94.6265 |  | -0.50025 | 1.3783 | 1.7335 | 234.9773 | 322.3951
10 | 2021-03-14 | TEM2 | 21.4517 | -119.3843 |  | 140.836 |  | -0.17969 | 1.3989 | 1.7639 | 235.2053 | 311.4347
11 | 2021-03-21 | TEM2 | 77.1398 | 2.5757 |  | 74.564 |  | 29.9485 | 1.3944 | 1.8022 | 248.0443 | 381.2247
12 | 2021-03-28 | TEM2 | 72.5545 | 11.2858 |  | 61.2687 |  | 6.4289 | 1.3818 | 1.7839 | 254.3037 | 384.0164
13 | 2021-04-04 | TEM2 | 34.2029 | -72.7567 |  | 106.9596 |  | -0.4701 | 1.3785 | 1.7869 | 259.5284 | 351.8192
14 | 2021-04-11 | TEM2 | 21.062 | -112.1257 |  | 133.1876 |  | -0.18784 | 1.3807 | 1.7222 | 260.9424 | 338.3162
15 | 2021-04-18 | TEM2 | 75.9119 | 33.1745 |  | 42.7374 |  | 2.2883 | 1.3844 | 1.627 | 264.9489 | 398.2524
16 | 2021-04-25 | TEM2 | 53.4317 | 27.3938 |  | 26.0379 |  | 1.9505 | 1.348 | 1.4462 | 267.8585 | 374.1979
17 | 2021-05-02 | TEM2 | 48.5215 | -106.0259 |  | 154.5474 |  | -0.45764 | 1.3315 | 1.4379 | 353.098 | 454.9122
18 | 2021-05-09 | TEM2 | 20.2544 | -145.2433 |  | 165.4977 |  | -0.13945 | 1.3132 | 1.4542 | 362.3274 | 436.6295
19 | 2021-05-16 | TEM2 | 47.764 | -112.0013 |  | 159.7653 |  | -0.42646 | 1.34 | 1.4823 | 368.2097 | 468.8241
20 | 2021-05-23 | TEM2 | 75.3019 | -19.0215 |  | 94.3233 |  | -3.9588 | 1.2917 | 1.3952 | 380.7053 | 510.4457
21 | 2021-05-30 | TEM2 | 59.4508 | -71.7362 |  | 131.1871 |  | -0.82874 | 1.2837 | 1.3276 | 393.3802 | 508.2604
22 | 2021-06-06 | TEM2 | 36.7951 | -26.5415 |  | 63.3365 |  | -1.3863 | 1.2458 | 1.4569 | 401.3101 | 491.7479
23 | 2021-06-13 | TEM2 | 43.5243 | -26.6087 |  | 70.133 |  | -1.6357 | 1.2973 | 1.4167 | 404.3373 | 500.1547
24 | 2021-06-20 | TEM2 | 33.0124 | -101.977 |  | 134.9894 |  | -0.32372 | 1.3322 | 1.4209 | 402.8727 | 491.5696
25 | 2021-06-27 | TEM2 | 13.6397 | -166.2911 |  | 179.9307 |  | -0.082023 | 1.3067 | 1.3834 | 400.7708 | 469.2693
26 | 2021-07-04 | TEM2 | 35.3343 | -128.7013 |  | 164.0357 |  | -0.27455 | 1.3516 | 1.458 | 404.4662 | 493.8631
27 | 2021-07-11 | TEM2 | 61.9188 | -26.8327 |  | 88.7515 |  | -2.3076 | 1.3281 | 1.3655 | 410.766 | 530.8289
28 | 2021-07-18 | TEM2 | 33.0022 | -21.1597 |  | 54.1619 |  | -1.5597 | 1.2788 | 1.3906 | 451.2313 | 543.2264
29 | 2021-07-25 | TEM2 | 16.7795 | -110.9392 |  | 127.7187 |  | -0.15125 | 1.2438 | 1.3943 | 499.4741 | 576.4628
30 | 2021-08-01 | TEM2 | 13.0831 | -172.6179 |  | 185.701 |  | -0.075792 | 1.2993 | 1.4316 | 505.281 | 576.8839
31 | 2021-08-08 | TEM2 | 32.7361 | -136.167 |  | 168.9032 |  | -0.24041 | 1.3491 | 1.4418 | 509.6148 | 599.9792
32 | 2021-08-15 | TEM2 | 63.7855 | -27.7855 |  | 91.571 |  | -2.2956 | 1.3084 | 1.4593 | 516.823 | 639.7917
33 | 2021-08-22 | TEM2 | 79.771 | -5.2043 |  | 84.9753 |  | -15.3279 | 1.3484 | 1.4263 | 542.7644 | 683.7426
34 | 2021-08-29 | TEM2 | 44.3332 | -57.3867 |  | 101.7198 |  | -0.77253 | 1.365 | 1.4744 | 588.1717 | 693.6729
35 | 2021-09-05 | TEM2 | 16.701 | -132.9701 |  | 149.6711 |  | -0.1256 | 1.3471 | 1.423 | 585.4251 | 660.2336
36 | 2021-09-12 | TEM2 | 33.7333 | -106.2905 |  | 140.0238 |  | -0.31737 | 1.3729 | 1.4675 | 587.5597 | 681.5461
37 | 2021-09-19 | TEM2 | 89.1388 | -31.9849 |  | 121.1237 |  | -2.7869 | 1.3584 | 1.424 | 594.1581 | 743.0605
38 | 2021-09-26 | TEM2 | 18.3443 | -132.6248 |  | 150.969 |  | -0.13832 | 1.3777 | 1.4354 | 592.9551 | 668.9732
39 | 2021-10-03 | TEM2 | 33.6818 | -13.2953 |  | 46.9771 |  | -2.5334 | 1.3818 | 1.4192 | 684.4177 | 779.4896
40 | 2021-10-10 | TEM2 | 128.7223 | 132.3082 | 128.7223 | -3.5859 |  | 0.9729 | 1.3576 | 1.424 | 704.5175 | 898.8449
41 | 2021-10-17 | TEM2 | 142.5386 | 147.311 | 142.5386 | -4.7725 |  | 0.9676 | 1.3643 | 1.4421 | 702.1045 | 906.6536
42 | 2021-10-24 | TEM2 | 92.3031 | 40.0253 |  | 52.2779 |  | 2.3061 | 1.3288 | 1.4661 | 705.3097 | 859.9179
43 | 2021-10-31 | TEM2 | 18.754 | -22.051 |  | 40.805 |  | -0.85048 | 1.3453 | 1.4276 | 699.1543 | 778.5759
44 | 2021-11-07 | TEM2 | 35.8429 | 9.8988 |  | 25.9441 |  | 3.6209 | 1.3571 | 1.4237 | 700.7038 | 795.443
45 | 2021-11-14 | TEM2 | 39.0708 | -3.2077 |  | 42.2785 |  | -12.1803 | 1.3621 | 1.4241 | 698.6621 | 795.8552
46 | 2021-11-21 | TEM2 | 92.8901 | 46.2345 |  | 46.6556 |  | 2.0091 | 1.3799 | 1.376 | 704.6368 | 857.795
47 | 2021-11-28 | TEM2 | 78.1527 | 54.7806 |  | 23.3721 |  | 1.4266 | 1.3435 | 1.356 | 714.4742 | 857.3363
48 | 2021-12-05 | TEM2 | 149.2499 | 139.5487 |  | 9.7012 |  | 1.0695 | 1.3538 | 1.3403 | 709.3372 | 921.0255
49 | 2021-12-12 | TEM2 | 105.8623 | 61.1487 |  | 44.7136 |  | 1.7312 | 1.3556 | 1.3601 | 711.058 | 879.2411
50 | 2021-12-19 | TEM2 | 18.3872 | 7.3297 |  | 11.0575 |  | 2.5086 | 1.341 | 1.3456 | 738.4219 | 819.8631
51 | 2021-12-26 | TEM2 | 21.8895 | 23.3665 | 21.8895 | -1.477 |  | 0.93679 | 1.3329 | 1.2952 | 745.6486 | 830.7173
52 | 2022-01-02 | TEM2 | 100.1062 | 108.4133 | 100.1062 | -8.3071 | -8.3071 | 0.92338 | 1.3469 | 1.3265 | 746.2287 | 911.9196
53 | 2022-01-09 | TEM2 | 21.1493 | 18.545 |  | 2.6043 | -5.7028 | 1.1404 | 1.3417 | 1.3414 | 789.3216 | 875.1042
54 | 2022-01-16 | TEM2 | 160.2768 | 164.7892 | 160.2768 | -4.5124 | -10.2152 | 0.97262 | 1.3549 | 1.3562 | 804.8971 | 1031.4286
55 | 2022-01-23 | TEM2 | 108.7617 | 113.7926 | 108.7617 | -5.0309 | -15.2461 | 0.95579 | 1.333 | 1.3359 | 811.237 | 988.3928
56 | 2022-01-30 | TEM2 | 20.6687 | 16.4324 |  | 4.2363 | -11.0098 | 1.2578 | 1.3444 | 1.3428 | 804.7539 | 889.6577
57 | 2022-02-06 | TEM2 | 131.4851 | 133.8263 | 131.4851 | -2.3412 | -13.351 | 0.98251 | 1.356 | 1.3536 | 857.0462 | 1055.5995
58 | 2022-02-13 | TEM2 | 28.2198 | 42.2351 | 28.2198 | -14.0152 | -27.3662 | 0.66816 | 1.3407 | 1.3437 | 912.8713 | 1011.1548
59 | 2022-02-20 | TEM2 | 159.0215 | 145.7442 |  | 13.2773 | -14.0889 | 1.0911 | 1.3451 | 1.3425 | 926.3718 | 1157.1756
60 | 2022-02-27 | TEM2 | 199.621 | 207.7197 | 199.621 | -8.0987 | -22.1876 | 0.96101 | 1.3466 | 1.3496 | 934.1912 | 1207.1198
61 | 2022-03-06 | TEM2 | 176.2733 | 152.8904 |  | 23.3829 | 1.1953 | 1.1529 | 1.3386 | 1.3368 | 959.234 | 1210.128
62 | 2022-03-13 | TEM2 | 116.9645 | 130.7154 | 116.9645 | -13.7509 | -12.5556 | 0.8948 | 1.3259 | 1.3246 | 963.1405 | 1156.5
0 | 2021-01-03 | TEM3 | 82.2075 | 1.7516 |  | 80.4559 |  | 46.9335 | 1.4108 | 1.8546 | 685.2383 | 841.3002
1 | 2021-01-10 | TEM3 | 86.9576 | -2.5374 |  | 89.495 |  | -34.2708 | 1.4195 | 1.8655 | 698.868 | 872.8748
2 | 2021-01-17 | TEM3 | 86.5913 | -4.0785 |  | 90.6698 |  | -21.231 | 1.4132 | 1.9613 | 706.8419 | 954.7258
3 | 2021-01-24 | TEM3 | 88.6038 | -0.033709 |  | 88.6375 |  | -2628.4524 | 1.4138 | 1.8973 | 707.6036 | 941.3194
4 | 2021-01-31 | TEM3 | 81.0612 | 0.63557 |  | 80.4256 |  | 127.5414 | 1.4304 | 1.8774 | 706.9414 | 863.9196
5 | 2021-02-07 | TEM3 | 79.4367 | 0.53986 |  | 78.8968 |  | 147.1432 | 1.4226 | 1.8857 | 699.1506 | 859.3542
6 | 2021-02-14 | TEM3 | 83.778 | 1.9315 |  | 81.8464 |  | 43.3741 | 1.403 | 1.8264 | 693.8816 | 872.3247
7 | 2021-02-21 | TEM3 | 85.1549 | 0.37131 |  | 84.7836 |  | 229.3379 | 1.3965 | 1.8307 | 708.5586 | 956.9937
8 | 2021-02-28 | TEM3 | 85.6339 | -8.3788 |  | 94.0126 |  | -10.2204 | 1.3977 | 1.7912 | 719.0559 | 904.1991
9 | 2021-03-07 | TEM3 | 83.6075 | -4.7921 |  | 88.3996 |  | -17.4471 | 1.3783 | 1.7335 | 712.1312 | 875.2737
10 | 2021-03-14 | TEM3 | 90.653 | -3.9646 |  | 94.6176 |  | -22.8658 | 1.3989 | 1.7639 | 704.6882 | 878.0758
11 | 2021-03-21 | TEM3 | 87.9198 | -4.5467 |  | 92.4666 |  | -19.3369 | 1.3944 | 1.8022 | 707.2213 | 890.9944
12 | 2021-03-28 | TEM3 | 83.5332 | -7.2605 |  | 90.7937 |  | -11.5052 | 1.3818 | 1.7839 | 711.0048 | 896.5953
13 | 2021-04-04 | TEM3 | 86.2345 | -2.4771 |  | 88.7116 |  | -34.8125 | 1.3785 | 1.7869 | 713.3854 | 894.2972
14 | 2021-04-11 | TEM3 | 87.1662 | -5.7236 |  | 92.8897 |  | -15.2293 | 1.3807 | 1.7222 | 723.6528 | 914.3326
15 | 2021-04-18 | TEM3 | 86.443 | -4.2854 |  | 90.7284 |  | -20.1715 | 1.3844 | 1.627 | 712.8193 | 951.3335
16 | 2021-04-25 | TEM3 | 80.6672 | -4.587 |  | 85.2542 |  | -17.5859 | 1.348 | 1.4462 | 712.3463 | 899.0859
17 | 2021-05-02 | TEM3 | 79.4058 | -5.6184 |  | 85.0242 |  | -14.1333 | 1.3315 | 1.4379 | 706.8536 | 867.3237
18 | 2021-05-09 | TEM3 | 76.5656 | -3.3266 |  | 79.8922 |  | -23.0164 | 1.3132 | 1.4542 | 710.7362 | 926.404
19 | 2021-05-16 | TEM3 | 80.5412 | -0.89713 |  | 81.4384 |  | -89.7763 | 1.34 | 1.4823 | 707.7868 | 936.0208
20 | 2021-05-23 | TEM3 | 74.9327 | 3.3787 |  | 71.554 |  | 22.1777 | 1.2917 | 1.3952 | 702.6922 | 913.205
21 | 2021-05-30 | TEM3 | 75.4087 | 3.1783 |  | 72.2304 |  | 23.7264 | 1.2837 | 1.3276 | 705.2583 | 961.9524
22 | 2021-06-06 | TEM3 | 71.0647 | 3.668 |  | 67.3967 |  | 19.3742 | 1.2458 | 1.4569 | 700.8096 | 879.9578
23 | 2021-06-13 | TEM3 | 72.2663 | 20.6565 |  | 51.6098 |  | 3.4985 | 1.2973 | 1.4167 | 693.7419 | 877.946
24 | 2021-06-20 | TEM3 | 73.8383 | 116.2088 | 73.8383 | -42.3705 |  | 0.63539 | 1.3322 | 1.4209 | 642.2808 | 871.2478
25 | 2021-06-27 | TEM3 | 76.3818 | 99.5765 | 76.3818 | -23.1947 |  | 0.76707 | 1.3067 | 1.3834 | 650.6291 | 862.0337
26 | 2021-07-04 | TEM3 | 77.8141 | 99.3345 | 77.8141 | -21.5203 |  | 0.78335 | 1.3516 | 1.458 | 655.4683 | 895.42
27 | 2021-07-11 | TEM3 | 76.2313 | 94.5499 | 76.2313 | -18.3187 |  | 0.80625 | 1.3281 | 1.3655 | 657.5528 | 851.7567
28 | 2021-07-18 | TEM3 | 78.0372 | 88.2209 | 78.0372 | -10.1837 |  | 0.88457 | 1.2788 | 1.3906 | 668.5418 | 853.4365
29 | 2021-07-25 | TEM3 | 76.6179 | 88.7864 | 76.6179 | -12.1685 |  | 0.86295 | 1.2438 | 1.3943 | 674.9812 | 873.1868
30 | 2021-08-01 | TEM3 | 78.2473 | 92.4255 | 78.2473 | -14.1782 |  | 0.8466 | 1.2993 | 1.4316 | 676.6749 | 894.8564
31 | 2021-08-08 | TEM3 | 81.9754 | 88.3578 | 81.9754 | -6.3824 |  | 0.92777 | 1.3491 | 1.4418 | 680.8965 | 935.2448
32 | 2021-08-15 | TEM3 | 79.0235 | 88.1137 | 79.0235 | -9.0902 |  | 0.89684 | 1.3084 | 1.4593 | 678.2305 | 898.8199
33 | 2021-08-22 | TEM3 | 81.558 | 86.7467 | 81.558 | -5.1887 |  | 0.94019 | 1.3484 | 1.4263 | 681.2382 | 934.9182
34 | 2021-08-29 | TEM3 | 84.4012 | 87.0615 | 84.4012 | -2.6603 |  | 0.96944 | 1.365 | 1.4744 | 683.1833 | 965.108
35 | 2021-09-05 | TEM3 | 85.4847 | 89.0893 | 85.4847 | -3.6045 |  | 0.95954 | 1.3471 | 1.423 | 679.8649 | 938.5387
36 | 2021-09-12 | TEM3 | 82.7705 | 88.5892 | 82.7705 | -5.8188 |  | 0.93432 | 1.3729 | 1.4675 | 674.4218 | 939.5889
37 | 2021-09-19 | TEM3 | 86.1195 | 86.3061 | 86.1195 | -0.1866 |  | 0.99784 | 1.3584 | 1.424 | 672.4598 | 916.3782
38 | 2021-09-26 | TEM3 | 87.8162 | 95.7528 | 87.8162 | -7.9366 |  | 0.91711 | 1.3777 | 1.4354 | 668.5886 | 892.3579
39 | 2021-10-03 | TEM3 | 88.023 | 89.5995 | 88.023 | -1.5764 |  | 0.98241 | 1.3818 | 1.4192 | 667.8753 | 858.5312
40 | 2021-10-10 | TEM3 | 88.7659 | 92.1656 | 88.7659 | -3.3997 |  | 0.96311 | 1.3576 | 1.424 | 671.9633 | 892.0062
41 | 2021-10-17 | TEM3 | 93.4948 | 92.8651 |  | 0.6297 |  | 1.0068 | 1.3643 | 1.4421 | 674.6973 | 967.1967
42 | 2021-10-24 | TEM3 | 88.8794 | 90.2304 | 88.8794 | -1.351 |  | 0.98503 | 1.3288 | 1.4661 | 678.909 | 999.7944
43 | 2021-10-31 | TEM3 | 88.4516 | 93.3031 | 88.4516 | -4.8515 |  | 0.948 | 1.3453 | 1.4276 | 679.1489 | 988.0715
44 | 2021-11-07 | TEM3 | 97.6333 | 89.5101 |  | 8.1232 |  | 1.0908 | 1.3571 | 1.4237 | 673.349 | 941.77
45 | 2021-11-14 | TEM3 | 96.2543 | 91.7867 |  | 4.4676 |  | 1.0487 | 1.3621 | 1.4241 | 676.4634 | 917.6771
46 | 2021-11-21 | TEM3 | 96.9913 | 91.5337 |  | 5.4576 |  | 1.0596 | 1.3799 | 1.376 | 683.0148 | 993.9899
47 | 2021-11-28 | TEM3 | 88.4902 | 86.7565 |  | 1.7337 |  | 1.02 | 1.3435 | 1.356 | 683.966 | 974.2232
48 | 2021-12-05 | TEM3 | 93.7588 | 88.9441 |  | 4.8147 |  | 1.0541 | 1.3538 | 1.3403 | 678.1578 | 910.8098
49 | 2021-12-12 | TEM3 | 94.1362 | 89.8449 |  | 4.2914 |  | 1.0478 | 1.3556 | 1.3601 | 674.3216 | 923.474
50 | 2021-12-19 | TEM3 | 88.5907 | 94.3692 | 88.5907 | -5.7785 |  | 0.93877 | 1.341 | 1.3456 | 672.8114 | 915.2076
51 | 2021-12-26 | TEM3 | 88.3742 | 89.8647 | 88.3742 | -1.4905 |  | 0.98341 | 1.3329 | 1.2952 | 673.7229 | 861.785
52 | 2022-01-02 | TEM3 | 93.2651 | 93.8569 | 93.2651 | -0.59181 | -0.59181 | 0.99369 | 1.3469 | 1.3265 | 668.1077 | 881.4665
53 | 2022-01-09 | TEM3 | 91.4309 | 91.2279 |  | 0.20295 | -0.38886 | 1.0022 | 1.3417 | 1.3414 | 679.4022 | 964.9412
54 | 2022-01-16 | TEM3 | 89.3148 | 89.6262 | 89.3148 | -0.31142 | -0.70028 | 0.99653 | 1.3549 | 1.3562 | 684.2223 | 1014.6458
55 | 2022-01-23 | TEM3 | 88.7095 | 89.2836 | 88.7095 | -0.57404 | -1.2743 | 0.99357 | 1.333 | 1.3359 | 682.429 | 996.9714
56 | 2022-01-30 | TEM3 | 89.8605 | 88.7971 |  | 1.0634 | -0.21089 | 1.012 | 1.3444 | 1.3428 | 676.7973 | 939.3668
57 | 2022-02-06 | TEM3 | 92.3519 | 92.9685 | 92.3519 | -0.61668 | -0.82757 | 0.99337 | 1.356 | 1.3536 | 673.8433 | 871.9613
58 | 2022-02-13 | TEM3 | 92.4763 | 91.8022 |  | 0.67409 | -0.15348 | 1.0073 | 1.3407 | 1.3437 | 679.4472 | 901.1741
59 | 2022-02-20 | TEM3 | 92.5871 | 92.722 | 92.5871 | -0.13492 | -0.2884 | 0.99854 | 1.3451 | 1.3425 | 675.8065 | 937.9859
60 | 2022-02-27 | TEM3 | 92.1504 | 92.657 | 92.1504 | -0.50659 | -0.79499 | 0.99453 | 1.3466 | 1.3496 | 684.502 | 981.2787
61 | 2022-03-06 | TEM3 | 91.8691 | 91.3734 |  | 0.49571 | -0.29929 | 1.0054 | 1.3386 | 1.3368 | 684.905 | 997.7991
62 | 2022-03-13 | TEM3 | 86.3477 | 86.7746 | 86.3477 | -0.4269 | -0.72619 | 0.99508 | 1.3259 | 1.3246 | 683.2826 | 984.65
0 | 2021-01-03 | TEM4 | 63.8873 | 352.1738 | 63.8873 | -288.2865 |  | 0.18141 | 1.4108 | 1.8546 | 21.9127 | 133.8715
1 | 2021-01-10 | TEM4 | 27.7164 | 219.6536 | 27.7164 | -191.9371 |  | 0.12618 | 1.4195 | 1.8655 | 17.3333 | 91.3843
2 | 2021-01-17 | TEM4 | 20.2246 | 266.1586 | 20.2246 | -245.934 |  | 0.075987 | 1.4132 | 1.9613 | 14.76 | 82.8635
3 | 2021-01-24 | TEM4 | 21.6044 | 213.9657 | 21.6044 | -192.3613 |  | 0.10097 | 1.4138 | 1.8973 | 15.7077 | 83.8352
4 | 2021-01-31 | TEM4 | 51.0904 | 279.4776 | 51.0904 | -228.3873 |  | 0.18281 | 1.4304 | 1.8774 | 18.7916 | 118.1488
5 | 2021-02-07 | TEM4 | 100.5414 | 403.8104 | 100.5414 | -303.2691 |  | 0.24898 | 1.4226 | 1.8857 | 24.5287 | 174.4338
6 | 2021-02-14 | TEM4 | 90.7452 | 320.173 | 90.7452 | -229.4278 |  | 0.28343 | 1.403 | 1.8264 | 24.892 | 162.9632
7 | 2021-02-21 | TEM4 | 21.0144 | 222.2252 | 21.0144 | -201.2108 |  | 0.094563 | 1.3965 | 1.8307 | 16.3288 | 84.5603
8 | 2021-02-28 | TEM4 | 18.8107 | 240.5323 | 18.8107 | -221.7216 |  | 0.078204 | 1.3977 | 1.7912 | 16.9086 | 84.9135
9 | 2021-03-07 | TEM4 | 95.8079 | 259.1248 | 95.8079 | -163.3169 |  | 0.36974 | 1.3783 | 1.7335 | 22.8128 | 166.7533
10 | 2021-03-14 | TEM4 | 151.7922 | 298.1255 | 151.7922 | -146.3333 |  | 0.50916 | 1.3989 | 1.7639 | 28.2235 | 226.6079
11 | 2021-03-21 | TEM4 | 67.5002 | 233.698 | 67.5002 | -166.1978 |  | 0.28884 | 1.3944 | 1.8022 | 20.1125 | 135.5004
12 | 2021-03-28 | TEM4 | 26.5409 | 261.3952 | 26.5409 | -234.8543 |  | 0.10154 | 1.3818 | 1.7839 | 14.6631 | 90.7403
13 | 2021-04-04 | TEM4 | 77.5933 | 236.1248 | 77.5933 | -158.5315 |  | 0.32861 | 1.3785 | 1.7869 | 23.2639 | 150.6183
14 | 2021-04-11 | TEM4 | 92.2351 | 288.8975 | 92.2351 | -196.6623 |  | 0.31927 | 1.3807 | 1.7222 | 21.082 | 161.9658
15 | 2021-04-18 | TEM4 | 25.4975 | 214.9568 | 25.4975 | -189.4592 |  | 0.11862 | 1.3844 | 1.627 | 16.8282 | 91.429
16 | 2021-04-25 | TEM4 | 40.7555 | 341.3919 | 40.7555 | -300.6364 |  | 0.11938 | 1.348 | 1.4462 | 17.9052 | 104.2031
17 | 2021-05-02 | TEM4 | 44.5562 | 352.1153 | 44.5562 | -307.5591 |  | 0.12654 | 1.3315 | 1.4379 | 18.3382 | 105.6994
18 | 2021-05-09 | TEM4 | 56.8964 | 248.3864 | 56.8964 | -191.49 |  | 0.22906 | 1.3132 | 1.4542 | 24.1838 | 124.3371
19 | 2021-05-16 | TEM4 | 68.6997 | 255.7126 | 68.6997 | -187.0129 |  | 0.26866 | 1.34 | 1.4823 | 22.4819 | 133.6695
20 | 2021-05-23 | TEM4 | 26.0898 | 301.3298 | 26.0898 | -275.24 |  | 0.086582 | 1.2917 | 1.3952 | 20.6018 | 89.5365
21 | 2021-05-30 | TEM4 | 50.3424 | 359.4988 | 50.3424 | -309.1564 |  | 0.14004 | 1.2837 | 1.3276 | 21.6157 | 115.8281
22 | 2021-06-06 | TEM4 | 18.2774 | 190.3246 | 18.2774 | -172.0472 |  | 0.096033 | 1.2458 | 1.4569 | 19.8868 | 81.8659
23 | 2021-06-13 | TEM4 | 14.6433 | 220.1626 | 14.6433 | -205.5193 |  | 0.066511 | 1.2973 | 1.4167 | 16.0558 | 70.795
24 | 2021-06-20 | TEM4 | 43.4014 | 259.1872 | 43.4014 | -215.7858 |  | 0.16745 | 1.3322 | 1.4209 | 21.9814 | 107.3802
25 | 2021-06-27 | TEM4 | 53.1363 | 221.58 | 53.1363 | -168.4437 |  | 0.23981 | 1.3067 | 1.3834 | 24.3349 | 118.4844
26 | 2021-07-04 | TEM4 | 70.089 | 256.9438 | 70.089 | -186.8548 |  | 0.27278 | 1.3516 | 1.458 | 25.6555 | 136.093
27 | 2021-07-11 | TEM4 | 14.9993 | 161.5814 | 14.9993 | -146.5821 |  | 0.092828 | 1.3281 | 1.3655 | 18.355 | 77.6421
28 | 2021-07-18 | TEM4 | 16.6061 | 309.0399 | 16.6061 | -292.4338 |  | 0.053734 | 1.2788 | 1.3906 | 20.2457 | 81.5464
29 | 2021-07-25 | TEM4 | 18.3273 | 266.7091 | 18.3273 | -248.3817 |  | 0.068717 | 1.2438 | 1.3943 | 20.1954 | 83.3847
30 | 2021-08-01 | TEM4 | 42.2078 | 250.4237 | 42.2078 | -208.2159 |  | 0.16855 | 1.2993 | 1.4316 | 23.5559 | 108.3973
31 | 2021-08-08 | TEM4 | 53.4827 | 224.3074 | 53.4827 | -170.8247 |  | 0.23843 | 1.3491 | 1.4418 | 22.1155 | 116.5484
32 | 2021-08-15 | TEM4 | 24.2653 | 137.3131 | 24.2653 | -113.0478 |  | 0.17672 | 1.3084 | 1.4593 | 20.0346 | 85.8929
33 | 2021-08-22 | TEM4 | 23.466 | 163.4773 | 23.466 | -140.0114 |  | 0.14354 | 1.3484 | 1.4263 | 15.0222 | 82.1972
34 | 2021-08-29 | TEM4 | 58.2925 | 157.372 | 58.2925 | -99.0796 |  | 0.37041 | 1.365 | 1.4744 | 21.4647 | 121.3168
35 | 2021-09-05 | TEM4 | 94.1744 | 100.6262 | 94.1744 | -6.4517 |  | 0.93588 | 1.3471 | 1.423 | 23.9214 | 157.8103
36 | 2021-09-12 | TEM4 | 87.9491 | 210.7811 | 87.9491 | -122.832 |  | 0.41725 | 1.3729 | 1.4675 | 24.6602 | 153.8408
37 | 2021-09-19 | TEM4 | 61.4386 | 145.1567 | 61.4386 | -83.7181 |  | 0.42326 | 1.3584 | 1.424 | 21.6756 | 122.8023
38 | 2021-09-26 | TEM4 | 153.1436 | 148.0306 |  | 5.1129 |  | 1.0345 | 1.3777 | 1.4354 | 32.3097 | 224.2738
39 | 2021-10-03 | TEM4 | 147.6131 | 206.5909 | 147.6131 | -58.9778 |  | 0.71452 | 1.3818 | 1.4192 | 25.6292 | 212.0603
40 | 2021-10-10 | TEM4 | 14.994 | 59.3175 | 14.994 | -44.3236 |  | 0.25277 | 1.3576 | 1.424 | 16.994 | 73.2357
41 | 2021-10-17 | TEM4 | 17.7067 | 124.3021 | 17.7067 | -106.5954 |  | 0.14245 | 1.3643 | 1.4421 | 18.5307 | 72.8346
42 | 2021-10-24 | TEM4 | 24.2722 | 105.1658 | 24.2722 | -80.8937 |  | 0.2308 | 1.3288 | 1.4661 | 14.8846 | 77.5459
43 | 2021-10-31 | TEM4 | 106.6185 | 75.7803 |  | 30.8382 |  | 1.4069 | 1.3453 | 1.4276 | 28.5575 | 170.2964
44 | 2021-11-07 | TEM4 | 166.7054 | 171.2463 | 166.7054 | -4.541 |  | 0.97348 | 1.3571 | 1.4237 | 27.2905 | 223.8748
45 | 2021-11-14 | TEM4 | 176.1958 | 127.1201 |  | 49.0757 |  | 1.3861 | 1.3621 | 1.4241 | 27.3576 | 234.4243
46 | 2021-11-21 | TEM4 | 87.953 | 83.5233 |  | 4.4296 |  | 1.053 | 1.3799 | 1.376 | 24.0194 | 146.2607
47 | 2021-11-28 | TEM4 | 59.9982 | 118.1776 | 59.9982 | -58.1794 |  | 0.5077 | 1.3435 | 1.356 | 19.1487 | 119.4397
48 | 2021-12-05 | TEM4 | 70.602 | 104.5039 | 70.602 | -33.9019 |  | 0.67559 | 1.3538 | 1.3403 | 26.4348 | 131.8409
49 | 2021-12-12 | TEM4 | 82.8224 | 159.5976 | 82.8224 | -76.7753 |  | 0.51894 | 1.3556 | 1.3601 | 24.3244 | 145.4665
50 | 2021-12-19 | TEM4 | 153.9438 | 115.34 |  | 38.6038 |  | 1.3347 | 1.341 | 1.3456 | 33.1758 | 225.8482
51 | 2021-12-26 | TEM4 | 178.6458 | 244.7329 | 178.6458 | -66.0871 |  | 0.72996 | 1.3329 | 1.2952 | 26.2163 | 243.1295
52 | 2022-01-02 | TEM4 | 44.3959 | 143.7199 | 44.3959 | -99.3241 | -99.3241 | 0.30891 | 1.3469 | 1.3265 | 22.5024 | 106.6384
53 | 2022-01-09 | TEM4 | 155.9456 | 155.929 |  | 0.016664 | -99.3074 | 1.0001 | 1.3417 | 1.3414 | 23.8308 | 218.5871
54 | 2022-01-16 | TEM4 | 16.986 | 7.3065 |  | 9.6795 | -89.6279 | 2.3248 | 1.3549 | 1.3562 | 17.3025 | 72.6176
55 | 2022-01-23 | TEM4 | 40.4054 | 65.8288 | 40.4054 | -25.4234 | -115.0513 | 0.6138 | 1.333 | 1.3359 | 23.4258 | 104.1188
56 | 2022-01-30 | TEM4 | 190.6538 | 182.1789 |  | 8.4749 | -106.5764 | 1.0465 | 1.3444 | 1.3428 | 28.2181 | 256.3311
57 | 2022-02-06 | TEM4 | 101.3672 | 103.8135 | 101.3672 | -2.4463 | -109.0227 | 0.97644 | 1.356 | 1.3536 | 27.0175 | 159.9801
58 | 2022-02-13 | TEM4 | 166.4727 | 136.3276 |  | 30.1452 | -78.8776 | 1.2211 | 1.3407 | 1.3437 | 24.1535 | 229.4085
59 | 2022-02-20 | TEM4 | 60.6842 | 90.3962 | 60.6842 | -29.712 | -108.5896 | 0.67131 | 1.3451 | 1.3425 | 19.0833 | 118.3943
60 | 2022-02-27 | TEM4 | 17.9551 | 3.5169 |  | 14.4381 | -94.1515 | 5.1053 | 1.3466 | 1.3496 | 25.0592 | 81.4522
61 | 2022-03-06 | TEM4 | 17.2811 | 11.8761 |  | 5.405 | -88.7465 | 1.4551 | 1.3386 | 1.3368 | 16.6343 | 73.0372
62 | 2022-03-13 | TEM4 | 15.2222 | 12.9861 |  | 2.2361 | -86.5104 | 1.1722 | 1.3259 | 1.3246 | 13.5189 | 70.6
0 | 2021-01-03 | TEM5 | 119.1097 | 440.3371 | 119.1097 | -321.2273 |  | 0.2705 | 1.4108 | 1.8546 | 18.3541 | 218.8017
1 | 2021-01-10 | TEM5 | 135.7952 | 290.6888 | 135.7952 | -154.8935 |  | 0.46715 | 1.4195 | 1.8655 | 14.7412 | 229.9675
2 | 2021-01-17 | TEM5 | 51.8359 | 327.8834 | 51.8359 | -276.0476 |  | 0.15809 | 1.4132 | 1.9613 | 10.7238 | 144.7869
3 | 2021-01-24 | TEM5 | 97.2456 | 324.1112 | 97.2456 | -226.8656 |  | 0.30004 | 1.4138 | 1.8973 | 7.4078 | 185.164
4 | 2021-01-31 | TEM5 | 111.3025 | 393.1231 | 111.3025 | -281.8206 |  | 0.28312 | 1.4304 | 1.8774 | 9.6464 | 204.5563
5 | 2021-02-07 | TEM5 | 80.4856 | 328.2944 | 80.4856 | -247.8088 |  | 0.24516 | 1.4226 | 1.8857 | 15.7949 | 181.0857
6 | 2021-02-14 | TEM5 | 58.3591 | 431.2291 | 58.3591 | -372.87 |  | 0.13533 | 1.403 | 1.8264 | 14.4812 | 153.5479
7 | 2021-02-21 | TEM5 | 72.607 | 346.1757 | 72.607 | -273.5687 |  | 0.20974 | 1.3965 | 1.8307 | 11.9948 | 165.8938
8 | 2021-02-28 | TEM5 | 113.188 | 337.3999 | 113.188 | -224.212 |  | 0.33547 | 1.3977 | 1.7912 | 9.3986 | 207.3066
9 | 2021-03-07 | TEM5 | 100.6908 | 309.1554 | 100.6908 | -208.4646 |  | 0.3257 | 1.3783 | 1.7335 | 8.5373 | 192.6449
10 | 2021-03-14 | TEM5 | 84.0316 | 414.0947 | 84.0316 | -330.0631 |  | 0.20293 | 1.3989 | 1.7639 | 12.4331 | 178.2773
11 | 2021-03-21 | TEM5 | 74.311 | 382.9304 | 74.311 | -308.6194 |  | 0.19406 | 1.3944 | 1.8022 | 9.9024 | 167.0803
12 | 2021-03-28 | TEM5 | 77.3424 | 344.4251 | 77.3424 | -267.0827 |  | 0.22456 | 1.3818 | 1.7839 | 13.1099 | 175.751
13 | 2021-04-04 | TEM5 | 88.2489 | 394.5014 | 88.2489 | -306.2525 |  | 0.2237 | 1.3785 | 1.7869 | 7.7354 | 182.7699
14 | 2021-04-11 | TEM5 | 85.4204 | 355.0428 | 85.4204 | -269.6225 |  | 0.24059 | 1.3807 | 1.7222 | 13.1279 | 182.806
15 | 2021-04-18 | TEM5 | 56.4846 | 297.2561 | 56.4846 | -240.7715 |  | 0.19002 | 1.3844 | 1.627 | 10.9409 | 152.6444
16 | 2021-04-25 | TEM5 | 67.7261 | 301.9346 | 67.7261 | -234.2086 |  | 0.22431 | 1.348 | 1.4462 | 17.7576 | 164.9818
17 | 2021-05-02 | TEM5 | 86.248 | 312.9309 | 86.248 | -226.6829 |  | 0.27561 | 1.3315 | 1.4379 | 17.6314 | 179.3598
18 | 2021-05-09 | TEM5 | 34.7327 | 367.2217 | 34.7327 | -332.4891 |  | 0.094582 | 1.3132 | 1.4542 | 11.5247 | 122.7274
19 | 2021-05-16 | TEM5 | 24.4546 | 350.0015 | 24.4546 | -325.5469 |  | 0.06987 | 1.34 | 1.4823 | 29.3148 | 124.4707
20 | 2021-05-23 | TEM5 | 44.8827 | 395.8869 | 44.8827 | -351.0041 |  | 0.11337 | 1.2917 | 1.3952 | 289.3168 | 413.1531
21 | 2021-05-30 | TEM5 | 44.5431 | 404.9895 | 44.5431 | -360.4463 |  | 0.10999 | 1.2837 | 1.3276 | 606.4868 | 734.7468
22 | 2021-06-06 | TEM5 | 14.3146 | 432.2188 | 14.3146 | -417.9042 |  | 0.033119 | 1.2458 | 1.4569 | 12.9876 | 100.0086
23 | 2021-06-13 | TEM5 | 35.9635 | 352.0495 | 35.9635 | -316.086 |  | 0.10215 | 1.2973 | 1.4167 | 17.7493 | 124.3574
24 | 2021-06-20 | TEM5 | 26.6426 | 446.4144 | 26.6426 | -419.7718 |  | 0.059681 | 1.3322 | 1.4209 | 12.4413 | 113.1608
25 | 2021-06-27 | TEM5 | 38.9938 | 274.8578 | 38.9938 | -235.864 |  | 0.14187 | 1.3067 | 1.3834 | 13.4503 | 127.4171
26 | 2021-07-04 | TEM5 | 20.8393 | 223.1086 | 20.8393 | -202.2692 |  | 0.093404 | 1.3516 | 1.458 | 10.3217 | 104.1816
27 | 2021-07-11 | TEM5 | 32.1763 | 144.6847 | 32.1763 | -112.5084 |  | 0.22239 | 1.3281 | 1.3655 | 15.0526 | 123.2772
28 | 2021-07-18 | TEM5 | 22.7053 | 130.6795 | 22.7053 | -107.9742 |  | 0.17375 | 1.2788 | 1.3906 | 18.2951 | 120.5484
29 | 2021-07-25 | TEM5 | 31.633 | 125.8323 | 31.633 | -94.1993 |  | 0.25139 | 1.2438 | 1.3943 | 17.6182 | 130.5082
30 | 2021-08-01 | TEM5 | 34.4483 | 165.5202 | 34.4483 | -131.0719 |  | 0.20812 | 1.2993 | 1.4316 | 15.0718 | 125.9488
31 | 2021-08-08 | TEM5 | 23.5356 | 98.4084 | 23.5356 | -74.8729 |  | 0.23916 | 1.3491 | 1.4418 | 11.3729 | 107.5877
32 | 2021-08-15 | TEM5 | 17.4264 | 106.4566 | 17.4264 | -89.0302 |  | 0.1637 | 1.3084 | 1.4593 | 11.0486 | 102.4963
33 | 2021-08-22 | TEM5 | 22.9895 | 33.7284 | 22.9895 | -10.739 |  | 0.6816 | 1.3484 | 1.4263 | 14.8349 | 116.7892
34 | 2021-08-29 | TEM5 | 22.2825 | 46.3431 | 22.2825 | -24.0606 |  | 0.48082 | 1.365 | 1.4744 | 12.0669 | 107.2281
35 | 2021-09-05 | TEM5 | 66.147 | 113.5249 | 66.147 | -47.3779 |  | 0.58266 | 1.3471 | 1.423 | 14.7704 | 153.1776
36 | 2021-09-12 | TEM5 | 29.0417 | 151.5904 | 29.0417 | -122.5488 |  | 0.19158 | 1.3729 | 1.4675 | 12.3069 | 114.6293
37 | 2021-09-19 | TEM5 | 28.5716 | 78.1737 | 28.5716 | -49.602 |  | 0.36549 | 1.3584 | 1.424 | 12.5772 | 111.4872
38 | 2021-09-26 | TEM5 | 53.3378 | 193.7966 | 53.3378 | -140.4588 |  | 0.27523 | 1.3777 | 1.4354 | 10.1239 | 130.8253
39 | 2021-10-03 | TEM5 | 87.0268 | 98.7795 | 87.0268 | -11.7527 |  | 0.88102 | 1.3818 | 1.4192 | 20.4795 | 175.2976
40 | 2021-10-10 | TEM5 | 81.4731 | 99.243 | 81.4731 | -17.7699 |  | 0.82095 | 1.3576 | 1.424 | 20.4542 | 173.986
41 | 2021-10-17 | TEM5 | 45.5736 | 104.2062 | 45.5736 | -58.6325 |  | 0.43734 | 1.3643 | 1.4421 | 13.2048 | 124.77
42 | 2021-10-24 | TEM5 | 26.8495 | 127.5776 | 26.8495 | -100.7281 |  | 0.21046 | 1.3288 | 1.4661 | 14.8217 | 109.1872
43 | 2021-10-31 | TEM5 | 27.0432 | 125.0171 | 27.0432 | -97.9739 |  | 0.21632 | 1.3453 | 1.4276 | 4.3213 | 102.0507
44 | 2021-11-07 | TEM5 | 58.5267 | 74.2304 | 58.5267 | -15.7037 |  | 0.78845 | 1.3571 | 1.4237 | 4.0632 | 136.5458
45 | 2021-11-14 | TEM5 | 63.1145 | 80.9485 | 63.1145 | -17.834 |  | 0.77969 | 1.3621 | 1.4241 | 6.3703 | 142.4127
46 | 2021-11-21 | TEM5 | 41.922 | 33.4949 |  | 8.4271 |  | 1.2516 | 1.3799 | 1.376 | 1.0291 | 117.746
47 | 2021-11-28 | TEM5 | 23.318 | 5.3487 |  | 17.9693 |  | 4.3595 | 1.3435 | 1.356 | 5.1579 | 111.0934
48 | 2021-12-05 | TEM5 | 45.2692 | -3.5533 |  | 48.8225 |  | -12.7399 | 1.3538 | 1.3403 | 0.42364 | 122.9742
49 | 2021-12-12 | TEM5 | 59.3619 | 65.7181 | 59.3619 | -6.3562 |  | 0.90328 | 1.3556 | 1.3601 | 4.948 | 143.3566
50 | 2021-12-19 | TEM5 | 36.437 | 110.0785 | 36.437 | -73.6415 |  | 0.33101 | 1.341 | 1.3456 | -0.16797 | 114.7137
51 | 2021-12-26 | TEM5 | 85.0104 | 78.4579 |  | 6.5525 |  | 1.0835 | 1.3329 | 1.2952 | 20.2798 | 174.9805
52 | 2022-01-02 | TEM5 | 147.9053 | 120.0511 |  | 27.8542 | 27.8542 | 1.232 | 1.3469 | 1.3265 | 20.7803 | 238.8819
53 | 2022-01-09 | TEM5 | 46.6578 | 56.1373 | 46.6578 | -9.4795 | 18.3747 | 0.83114 | 1.3417 | 1.3414 | 16.7628 | 129.5977
54 | 2022-01-16 | TEM5 | 29.8918 | 31.6544 | 29.8918 | -1.7627 | 16.612 | 0.94431 | 1.3549 | 1.3562 | 14.7547 | 112.3462
55 | 2022-01-23 | TEM5 | 27.8479 | 39.085 | 27.8479 | -11.2371 | 5.3749 | 0.7125 | 1.333 | 1.3359 | 9.3792 | 106.4474
56 | 2022-01-30 | TEM5 | 41.5818 | 23.3682 |  | 18.2136 | 23.5885 | 1.7794 | 1.3444 | 1.3428 | 15.588 | 122.2331
57 | 2022-02-06 | TEM5 | 112.0977 | 116.7646 | 112.0977 | -4.6668 | 18.9216 | 0.96003 | 1.356 | 1.3536 | 19.5969 | 197.7949
58 | 2022-02-13 | TEM5 | 134.024 | 127.1956 |  | 6.8283 | 25.75 | 1.0537 | 1.3407 | 1.3437 | 23.8029 | 226.1488
59 | 2022-02-20 | TEM5 | 67.2412 | 66.8791 |  | 0.36208 | 26.1121 | 1.0054 | 1.3451 | 1.3425 | 17.8005 | 152.3798
60 | 2022-02-27 | TEM5 | 31.5336 | 32.5124 | 31.5336 | -0.97884 | 25.1332 | 0.96989 | 1.3466 | 1.3496 | 6.2262 | 104.7738
61 | 2022-03-06 | TEM5 | 31.1593 | 27.7835 |  | 3.3758 | 28.509 | 1.1215 | 1.3386 | 1.3368 | 15.7523 | 115.4634
62 | 2022-03-13 | TEM5 | 26.5921 | 29.1037 | 26.5921 | -2.5116 | 25.9974 | 0.9137 | 1.3259 | 1.3246 | 19.3827 | 117.3
0 | 2021-01-03 | Total | 573.5074 | 1414.6474 | 573.5074 | -841.14 |  | 0.40541 | 1.4108 | 1.8546 | 1895.1951 | 2673.7735
1 | 2021-01-10 | Total | 588.4181 | 1449.2399 | 588.4181 | -860.8218 |  | 0.40602 | 1.4195 | 1.8655 | 1930.1357 | 2739.8621
2 | 2021-01-17 | Total | 499.706 | 1559.9448 | 499.706 | -1060.2388 |  | 0.32034 | 1.4132 | 1.9613 | 1934.4809 | 2733.7888
3 | 2021-01-24 | Total | 546.6636 | 1481.8509 | 546.6636 | -935.1873 |  | 0.36891 | 1.4138 | 1.8973 | 1934.4392 | 2734.9303
4 | 2021-01-31 | Total | 559.0765 | 1426.8609 | 559.0765 | -867.7844 |  | 0.39182 | 1.4304 | 1.8774 | 1941.3755 | 2777.0194
5 | 2021-02-07 | Total | 550.3528 | 1469.4493 | 550.3528 | -919.0965 |  | 0.37453 | 1.4226 | 1.8857 | 1984.7667 | 2823.6191
6 | 2021-02-14 | Total | 579.4155 | 1427.0189 | 579.4155 | -847.6033 |  | 0.40603 | 1.403 | 1.8264 | 2001.7033 | 2808.3432
7 | 2021-02-21 | Total | 547.2596 | 1442.5346 | 547.2596 | -895.275 |  | 0.37937 | 1.3965 | 1.8307 | 2061.9753 | 2879.5735
8 | 2021-02-28 | Total | 560.2732 | 1390.6785 | 560.2732 | -830.4053 |  | 0.40288 | 1.3977 | 1.7912 | 2110.3837 | 2949.6919
9 | 2021-03-07 | Total | 594.222 | 1347.8638 | 594.222 | -753.6418 |  | 0.44086 | 1.3783 | 1.7335 | 2121.7726 | 2924.4162
10 | 2021-03-14 | Total | 652.809 | 1426.4781 | 652.809 | -773.6691 |  | 0.45764 | 1.3989 | 1.7639 | 2119.3826 | 2964.7382
11 | 2021-03-21 | Total | 585.2804 | 1451.109 | 585.2804 | -865.8287 |  | 0.40333 | 1.3944 | 1.8022 | 2123.114 | 2960.5438
12 | 2021-03-28 | Total | 529.7065 | 1387.5573 | 529.7065 | -857.8508 |  | 0.38175 | 1.3818 | 1.7839 | 2133.4179 | 2947.9423
13 | 2021-04-04 | Total | 567.2304 | 1444.9211 | 567.2304 | -877.6907 |  | 0.39257 | 1.3785 | 1.7869 | 2148.7962 | 2962.0344
14 | 2021-04-11 | Total | 573.1677 | 1312.5822 | 573.1677 | -739.4145 |  | 0.43667 | 1.3807 | 1.7222 | 2164.9709 | 2989.1587
15 | 2021-04-18 | Total | 516.2102 | 1038.2926 | 516.2102 | -522.0824 |  | 0.49717 | 1.3844 | 1.627 | 2151.8866 | 2979.1076
16 | 2021-04-25 | Total | 499.1703 | 712.0185 | 499.1703 | -212.8483 |  | 0.70106 | 1.348 | 1.4462 | 2168.604 | 2923.3497
17 | 2021-05-02 | Total | 516.4887 | 755.9194 | 516.4887 | -239.4307 |  | 0.68326 | 1.3315 | 1.4379 | 2251.356 | 2997.688
18 | 2021-05-09 | Total | 424.4683 | 744.2936 | 424.4683 | -319.8253 |  | 0.5703 | 1.3132 | 1.4542 | 2268.7764 | 2979.348
19 | 2021-05-16 | Total | 490.7673 | 816.7062 | 490.7673 | -325.9388 |  | 0.60091 | 1.34 | 1.4823 | 2290.6407 | 3069.4443
20 | 2021-05-23 | Total | 462.9403 | 728.9249 | 462.9403 | -265.9846 |  | 0.6351 | 1.2917 | 1.3952 | 2570.0539 | 3319.6317
21 | 2021-05-30 | Total | 479.3428 | 606.7321 | 479.3428 | -127.3892 |  | 0.79004 | 1.2837 | 1.3276 | 2903.8606 | 3727.6925
22 | 2021-06-06 | Total | 281.4918 | 769.2447 | 281.4918 | -487.7529 |  | 0.36593 | 1.2458 | 1.4569 | 2310.2135 | 2878.0322
23 | 2021-06-13 | Total | 370.2832 | 645.4889 | 370.2832 | -275.2057 |  | 0.57365 | 1.2973 | 1.4167 | 2305.6376 | 2991.1271
24 | 2021-06-20 | Total | 413.513 | 613.0189 | 413.513 | -199.5059 |  | 0.67455 | 1.3322 | 1.4209 | 2251.0062 | 2998.8718
25 | 2021-06-27 | Total | 397.8708 | 571.5827 | 397.8708 | -173.7119 |  | 0.69609 | 1.3067 | 1.3834 | 2264.0523 | 2958.3592
26 | 2021-07-04 | Total | 479.2868 | 721.0093 | 479.2868 | -241.7226 |  | 0.66474 | 1.3516 | 1.458 | 2272.2471 | 3071.1768
27 | 2021-07-11 | Total | 446.7558 | 531.8673 | 446.7558 | -85.1115 |  | 0.83998 | 1.3281 | 1.3655 | 2277.2337 | 3024.3382
28 | 2021-07-18 | Total | 356.2924 | 616.725 | 356.2924 | -260.4326 |  | 0.57772 | 1.2788 | 1.3906 | 2329.4904 | 2978.8673
29 | 2021-07-25 | Total | 284.9061 | 643.647 | 284.9061 | -358.7409 |  | 0.44264 | 1.2438 | 1.3943 | 2384.7946 | 2966.2924
30 | 2021-08-01 | Total | 407.3597 | 724.2377 | 407.3597 | -316.878 |  | 0.56247 | 1.2993 | 1.4316 | 2395.2281 | 3112.0508
31 | 2021-08-08 | Total | 496.2334 | 718.3885 | 496.2334 | -222.1551 |  | 0.69076 | 1.3491 | 1.4418 | 2397.273 | 3234.1457
32 | 2021-08-15 | Total | 399.1631 | 760.5406 | 399.1631 | -361.3775 |  | 0.52484 | 1.3084 | 1.4593 | 2395.4164 | 3134.1436
33 | 2021-08-22 | Total | 510.0196 | 698.6197 | 510.0196 | -188.6001 |  | 0.73004 | 1.3484 | 1.4263 | 2419.6751 | 3262.6828
34 | 2021-08-29 | Total | 541.7538 | 811.6391 | 541.7538 | -269.8853 |  | 0.66748 | 1.365 | 1.4744 | 2467.0115 | 3367.4521
35 | 2021-09-05 | Total | 547.0535 | 734.851 | 547.0535 | -187.7975 |  | 0.74444 | 1.3471 | 1.423 | 2472.4708 | 3330.5459
36 | 2021-09-12 | Total | 577.423 | 810.7308 | 577.423 | -233.3078 |  | 0.71223 | 1.3729 | 1.4675 | 2467.9255 | 3388.3194
37 | 2021-09-19 | Total | 590.0242 | 752.4488 | 590.0242 | -162.4246 |  | 0.78414 | 1.3584 | 1.424 | 2474.1878 | 3360.8246
38 | 2021-09-26 | Total | 673.9903 | 817.0631 | 673.9903 | -143.0729 |  | 0.82489 | 1.3777 | 1.4354 | 2478.9879 | 3415.3588
39 | 2021-10-03 | Total | 731.8957 | 828.408 | 731.8957 | -96.5123 |  | 0.8835 | 1.3818 | 1.4192 | 2578.7661 | 3563.2359
40 | 2021-10-10 | Total | 668.6784 | 841.0654 | 668.6784 | -172.387 |  | 0.79504 | 1.3576 | 1.424 | 2596.7887 | 3525.4714
41 | 2021-10-17 | Total | 656.3787 | 857.8256 | 656.3787 | -201.4469 |  | 0.76517 | 1.3643 | 1.4421 | 2589.3003 | 3532.5567
42 | 2021-10-24 | Total | 520.9323 | 877.4077 | 520.9323 | -356.4755 |  | 0.59372 | 1.3288 | 1.4661 | 2596.808 | 3450.5993
43 | 2021-10-31 | Total | 518.7705 | 732.1782 | 518.7705 | -213.4077 |  | 0.70853 | 1.3453 | 1.4276 | 2592.2707 | 3487.3871
44 | 2021-11-07 | Total | 667.6728 | 839.8837 | 667.6728 | -172.2109 |  | 0.79496 | 1.3571 | 1.4237 | 2585.9242 | 3509.3835
45 | 2021-11-14 | Total | 673.6008 | 834.0934 | 673.6008 | -160.4926 |  | 0.80758 | 1.3621 | 1.4241 | 2590.3923 | 3528.3598
46 | 2021-11-21 | Total | 628.8265 | 618.6884 |  | 10.1382 |  | 1.0164 | 1.3799 | 1.376 | 2599.2929 | 3586.6646
47 | 2021-11-28 | Total | 525.5628 | 558.1907 | 525.5628 | -32.6279 |  | 0.94155 | 1.3435 | 1.356 | 2614.9784 | 3513.1641
48 | 2021-12-05 | Total | 656.8681 | 621.7457 |  | 35.1224 |  | 1.0565 | 1.3538 | 1.3403 | 2597.8572 | 3517.0058
49 | 2021-12-12 | Total | 638.7619 | 650.3941 | 638.7619 | -11.6322 |  | 0.98212 | 1.3556 | 1.3601 | 2601.8456 | 3527.181
50 | 2021-12-19 | Total | 579.3182 | 591.4898 | 579.3182 | -12.1715 |  | 0.97942 | 1.341 | 1.3456 | 2633.3239 | 3531.1683
51 | 2021-12-26 | Total | 666.1781 | 565.8989 |  | 100.2792 |  | 1.1772 | 1.3329 | 1.2952 | 2656.154 | 3540.4931
52 | 2022-01-02 | Total | 689.4408 | 635.4384 |  | 54.0024 | 54.0024 | 1.085 | 1.3469 | 1.3265 | 2647.0322 | 3565.2636
53 | 2022-01-09 | Total | 608.0082 | 607.2837 |  | 0.72449 | 54.7269 | 1.0012 | 1.3417 | 1.3414 | 2704.4898 | 3628.5396
54 | 2022-01-16 | Total | 595.0181 | 598.5448 | 595.0181 | -3.5267 | 51.2001 | 0.99411 | 1.3549 | 1.3562 | 2720.8841 | 3686.6096
55 | 2022-01-23 | Total | 555.5384 | 563.4667 | 555.5384 | -7.9283 | 43.2719 | 0.98593 | 1.333 | 1.3359 | 2729.262 | 3638.0008
56 | 2022-01-30 | Total | 637.1946 | 632.7536 |  | 4.441 | 47.7129 | 1.007 | 1.3444 | 1.3428 | 2728.0307 | 3667.6125
57 | 2022-02-06 | Total | 743.4994 | 736.769 |  | 6.7304 | 54.4433 | 1.0091 | 1.356 | 1.3536 | 2778.5933 | 3767.7463
58 | 2022-02-13 | Total | 724.177 | 732.6952 | 724.177 | -8.5182 | 45.9251 | 0.98837 | 1.3407 | 1.3437 | 2840.036 | 3807.7195
59 | 2022-02-20 | Total | 676.726 | 669.4232 |  | 7.3028 | 53.2279 | 1.0109 | 1.3451 | 1.3425 | 2838.372 | 3817.9132
60 | 2022-02-27 | Total | 647.0608 | 655.3992 | 647.0608 | -8.3384 | 44.8895 | 0.98728 | 1.3466 | 1.3496 | 2852.7327 | 3841.5769
61 | 2022-03-06 | Total | 617.2477 | 612.0733 |  | 5.1744 | 50.0639 | 1.0085 | 1.3386 | 1.3368 | 2885.4945 | 3862.6182
62 | 2022-03-13 | Total | 518.3009 | 514.319 |  | 3.9819 | 54.0458 | 1.0077 | 1.3259 | 1.3246 | 2888.5522 | 3830.05